## Instructions
DER Security Corp
IEEE-1547 Protocol Information Conformance Statement (PICS)
For manufacturers of DER devices that must comply with IEEE 1547-2018 and UL 1741 SB.
This file was generated by SunSpec Dashboard or DER Security LabTest software. It is used to prepare and submit a product for testing at a Nationally Recognized Testing Lab (for electrical function validation and certification) or a SunSpec Authorized Testing laboratory (for SunSpec Modbus and/or IEEE 2030.5 communication protocol validation and certification). Some data is input by the user into the SunSpec Dashboard or DER Security LabTest software prior to autogenerating this spreadsheet and some data is read from Equipment Under Test (EUT) by SunSpec Dashboard or DER Security LabTest software after the spreadsheet is generated.
The Product and Testing Info tab contains general information about the unit under test, the manufacturer of the product, and the test laboratory network setup. It also contains an area for test laboratory personnel to enter information about an IEEE 1547 test that has previously been run on the unit under test.
The Test Lab Settings tab contains information about the testing laboratory and test engineer that ran a test. Data is input to this tab by the test engineer after a test run is completed.
The IEEE 1547 Electrical Test Setup tab contains information needed to configure the EUT for electrical testing according the IEEE 1547.1 standard. Most parameters are defined in the IEEE 1547.1 "Test Requirements" section (section 5.14.2) and some were by DER Security Corp to facilitate electrical test setup.
Numerical Tab names refer to the specific SunSpec Modbus models contained in the EUT and tab names that start with "2030.5 CSIP-" refer to specific IEEE 2030.5 capabilities of the product that the EUT will be evaluated against.
DER Security Corp License Agreement and Copyright
This document and the information contained herein is provided on an "AS IS" basis and the DER Security Corp DISCLAIMS ALL WARRANTIES, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY WARRANTY THAT THE USE OF THE INFORMATION HEREIN WILL NOT INFRINGE ANY OWNERSHIP RIGHTS OR ANY IMPLIED WARRANTIES OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE.
This document may be used, copied, and furnished to others, without restrictions of any kind, provided that this document itself may not be modified in anyway, except as needed by the DER Security Corp Technical Committee and as governed by the DER Security Corp IPR Policy. The complete policy of DER Security Corp can be found at https://www.dersec.io/.

## Product and Testing Info
Product Information
Product Type | Gateway
Manufacturer Name | Carlo Gavazzi Controls
Product Name | EMS
Product Model Numbers
Submitter Information
Full Name | Gabriele Pellegrini
Job Title | Engineer
Company Name | Carlo Gavazzi
Relationship to Manufacturer | Employee
Email | gabriele.pellegrini@gavazziacbu.it
Phone | +39 0437 355811
Device Under Test Information
Test Type | SunSpec Modbus Conformance Certification
Firmware Version Tested | EMS_1.0.0.0.251009.140528
Firmware Checksum (in hex) | ad5e9441a744ea5c2e9109c005cfb8fb
Interface Type | RTU
If RTU
Interface Name | COM5
Unit ID | 1
Baud Rate | 9600
Parity | None
Timeout (secs) | 100
If Modbus TCP
IP Address | 10.1.4.2
IP Port | 502
Unit ID | 1
If IEEE 2030.5
IP Address
IP Port
Poll Rate
Client PIN
Timeout (secs)
SunSpec Certificate Number | SM-000048
Certificate Signer Name | Erin Mahan
Certificate Issued Date | 2025-10-20
Certificate Archive Location | https://sunspec.org/wp-content/uploads/2009/03/Carlo-Gavazzi_Modbus_Certificate_SM000048.pdf

## 1
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40002 | ID |  | 1 | R | 1 | 1
40003 | L |  | 66 | R
40004 | Mn |  | CARLO-GAVAZZI-CONTROLS | R
40020 | Md |  | EMS10MV5S1X | R
40036 | Opt |  | unimplemented | R
40044 | Vr |  | 1.0.0 | R
40052 | SN |  | BZ025052201RD | R
40068 | DA |  | unimplemented | RW
40069 | Pad |  | 32768 | R

## 211
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40070 | ID |  | 211 | R
40071 | L |  | 124 | R
40072 | A |  | supported | R
40074 | AphA |  | supported | R
40076 | AphB |  | unimplemented | R
40078 | AphC |  | unimplemented | R
40080 | PhV |  | supported | R
40082 | PhVphA |  | unimplemented | R
40084 | PhVphB |  | unimplemented | R
40086 | PhVphC |  | unimplemented | R
40088 | PPV |  | unimplemented | R
40090 | PPVphAB |  | unimplemented | R
40092 | PPVphBC |  | unimplemented | R
40094 | PPVphCA |  | unimplemented | R
40096 | Hz |  | supported | R
40098 | W |  | supported | R
40100 | WphA |  | unimplemented | R
40102 | WphB |  | unimplemented | R
40104 | WphC |  | unimplemented | R
40106 | VA |  | supported | R
40108 | VAphA |  | unimplemented | R
40110 | VAphB |  | unimplemented | R
40112 | VAphC |  | unimplemented | R
40114 | VAR |  | supported | R
40116 | VARphA |  | unimplemented | R
40118 | VARphB |  | unimplemented | R
40120 | VARphC |  | unimplemented | R
40122 | PF |  | supported | R
40124 | PFphA |  | unimplemented | R
40126 | PFphB |  | unimplemented | R
40128 | PFphC |  | unimplemented | R
40130 | TotWhExp |  | supported | R
40132 | TotWhExpPhA |  | unimplemented | R
40134 | TotWhExpPhB |  | unimplemented | R
40136 | TotWhExpPhC |  | unimplemented | R
40138 | TotWhImp |  | supported | R
40140 | TotWhImpPhA |  | unimplemented | R
40142 | TotWhImpPhB |  | unimplemented | R
40144 | TotWhImpPhC |  | unimplemented | R
40146 | TotVAhExp |  | unimplemented | R
40148 | TotVAhExpPhA |  | unimplemented | R
40150 | TotVAhExpPhB |  | unimplemented | R
40152 | TotVAhExpPhC |  | unimplemented | R
40154 | TotVAhImp |  | supported | R
40156 | TotVAhImpPhA |  | unimplemented | R
40158 | TotVAhImpPhB |  | unimplemented | R
40160 | TotVAhImpPhC |  | unimplemented | R
40162 | TotVArhImpQ1 |  | supported | R
40164 | TotVArhImpQ1phA |  | unimplemented | R
40166 | TotVArhImpQ1phB |  | unimplemented | R
40168 | TotVArhImpQ1phC |  | unimplemented | R
40170 | TotVArhImpQ2 |  | supported | R
40172 | TotVArhImpQ2phA |  | unimplemented | R
40174 | TotVArhImpQ2phB |  | unimplemented | R
40176 | TotVArhImpQ2phC |  | unimplemented | R
40178 | TotVArhExpQ3 |  | supported | R
40180 | TotVArhExpQ3phA |  | unimplemented | R
40182 | TotVArhExpQ3phB |  | unimplemented | R
40184 | TotVArhExpQ3phC |  | unimplemented | R
40186 | TotVArhExpQ4 |  | supported | R
40188 | TotVArhExpQ4phA |  | unimplemented | R
40190 | TotVArhExpQ4phB |  | unimplemented | R
40192 | TotVArhExpQ4phC |  | unimplemented | R
40194 | Evt |  | supported | R
|  | M_EVENT_Power_Failure | supported
|  | M_EVENT_Under_Voltage | supported
|  | M_EVENT_Low_PF | supported
|  | M_EVENT_Over_Current | supported
|  | M_EVENT_Over_Voltage | supported
|  | M_EVENT_Missing_Sensor | supported
|  | M_EVENT_Reserved1 | supported
|  | M_EVENT_Reserved2 | supported
|  | M_EVENT_Reserved3 | supported
|  | M_EVENT_Reserved4 | supported
|  | M_EVENT_Reserved5 | supported
|  | M_EVENT_Reserved6 | supported
|  | M_EVENT_Reserved7 | supported
|  | M_EVENT_Reserved8 | supported
|  | M_EVENT_OEM01 | supported
|  | M_EVENT_OEM02 | supported
|  | M_EVENT_OEM03 | supported
|  | M_EVENT_OEM04 | supported
|  | M_EVENT_OEM05 | supported
|  | M_EVENT_OEM06 | supported
|  | M_EVENT_OEM07 | supported
|  | M_EVENT_OEM08 | supported
|  | M_EVENT_OEM09 | supported
|  | M_EVENT_OEM10 | supported
|  | M_EVENT_OEM11 | supported
|  | M_EVENT_OEM12 | supported
|  | M_EVENT_OEM13 | supported
|  | M_EVENT_OEM14 | supported
|  | M_EVENT_OEM15 | supported

## 212
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40070 | ID |  | 212 | R
40071 | L |  | 124 | R
40072 | A |  | supported | R
40074 | AphA |  | supported | R
40076 | AphB |  | supported | R
40078 | AphC |  | unimplemented | R
40080 | PhV |  | supported | R
40082 | PhVphA |  | supported | R
40084 | PhVphB |  | supported | R
40086 | PhVphC |  | unimplemented | R
40088 | PPV |  | supported | R
40090 | PPVphAB |  | supported | R
40092 | PPVphBC |  | unimplemented | R
40094 | PPVphCA |  | unimplemented | R
40096 | Hz |  | supported | R
40098 | W |  | supported | R
40100 | WphA |  | supported | R
40102 | WphB |  | supported | R
40104 | WphC |  | unimplemented | R
40106 | VA |  | supported | R
40108 | VAphA |  | supported | R
40110 | VAphB |  | supported | R
40112 | VAphC |  | unimplemented | R
40114 | VAR |  | supported | R
40116 | VARphA |  | supported | R
40118 | VARphB |  | supported | R
40120 | VARphC |  | unimplemented | R
40122 | PF |  | supported | R
40124 | PFphA |  | supported | R
40126 | PFphB |  | supported | R
40128 | PFphC |  | unimplemented | R
40130 | TotWhExp |  | supported | R
40132 | TotWhExpPhA |  | supported | R
40134 | TotWhExpPhB |  | supported | R
40136 | TotWhExpPhC |  | unimplemented | R
40138 | TotWhImp |  | supported | R
40140 | TotWhImpPhA |  | supported | R
40142 | TotWhImpPhB |  | supported | R
40144 | TotWhImpPhC |  | unimplemented | R
40146 | TotVAhExp |  | unimplemented | R
40148 | TotVAhExpPhA |  | unimplemented | R
40150 | TotVAhExpPhB |  | unimplemented | R
40152 | TotVAhExpPhC |  | unimplemented | R
40154 | TotVAhImp |  | supported | R
40156 | TotVAhImpPhA |  | unimplemented | R
40158 | TotVAhImpPhB |  | unimplemented | R
40160 | TotVAhImpPhC |  | unimplemented | R
40162 | TotVArhImpQ1 |  | supported | R
40164 | TotVArhImpQ1phA |  | unimplemented | R
40166 | TotVArhImpQ1phB |  | unimplemented | R
40168 | TotVArhImpQ1phC |  | unimplemented | R
40170 | TotVArhImpQ2 |  | supported | R
40172 | TotVArhImpQ2phA |  | unimplemented | R
40174 | TotVArhImpQ2phB |  | unimplemented | R
40176 | TotVArhImpQ2phC |  | unimplemented | R
40178 | TotVArhExpQ3 |  | supported | R
40180 | TotVArhExpQ3phA |  | unimplemented | R
40182 | TotVArhExpQ3phB |  | unimplemented | R
40184 | TotVArhExpQ3phC |  | unimplemented | R
40186 | TotVArhExpQ4 |  | supported | R
40188 | TotVArhExpQ4phA |  | unimplemented | R
40190 | TotVArhExpQ4phB |  | unimplemented | R
40192 | TotVArhExpQ4phC |  | unimplemented | R
40194 | Evt |  | supported | R
|  | M_EVENT_Power_Failure | supported
|  | M_EVENT_Under_Voltage | supported
|  | M_EVENT_Low_PF | supported
|  | M_EVENT_Over_Current | supported
|  | M_EVENT_Over_Voltage | supported
|  | M_EVENT_Missing_Sensor | supported
|  | M_EVENT_Reserved1 | supported
|  | M_EVENT_Reserved2 | supported
|  | M_EVENT_Reserved3 | supported
|  | M_EVENT_Reserved4 | supported
|  | M_EVENT_Reserved5 | supported
|  | M_EVENT_Reserved6 | supported
|  | M_EVENT_Reserved7 | supported
|  | M_EVENT_Reserved8 | supported
|  | M_EVENT_OEM01 | supported
|  | M_EVENT_OEM02 | supported
|  | M_EVENT_OEM03 | supported
|  | M_EVENT_OEM04 | supported
|  | M_EVENT_OEM05 | supported
|  | M_EVENT_OEM06 | supported
|  | M_EVENT_OEM07 | supported
|  | M_EVENT_OEM08 | supported
|  | M_EVENT_OEM09 | supported
|  | M_EVENT_OEM10 | supported
|  | M_EVENT_OEM11 | supported
|  | M_EVENT_OEM12 | supported
|  | M_EVENT_OEM13 | supported
|  | M_EVENT_OEM14 | supported
|  | M_EVENT_OEM15 | supported

## 213
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40070 | ID |  | 213 | R
40071 | L |  | 124 | R
40072 | A |  | supported | R
40074 | AphA |  | supported | R
40076 | AphB |  | supported | R
40078 | AphC |  | supported | R
40080 | PhV |  | supported | R
40082 | PhVphA |  | supported | R
40084 | PhVphB |  | supported | R
40086 | PhVphC |  | supported | R
40088 | PPV |  | supported | R
40090 | PPVphAB |  | supported | R
40092 | PPVphBC |  | supported | R
40094 | PPVphCA |  | supported | R
40096 | Hz |  | supported | R
40098 | W |  | supported | R
40100 | WphA |  | supported | R
40102 | WphB |  | supported | R
40104 | WphC |  | supported | R
40106 | VA |  | supported | R
40108 | VAphA |  | supported | R
40110 | VAphB |  | supported | R
40112 | VAphC |  | supported | R
40114 | VAR |  | supported | R
40116 | VARphA |  | supported | R
40118 | VARphB |  | supported | R
40120 | VARphC |  | supported | R
40122 | PF |  | supported | R
40124 | PFphA |  | supported | R
40126 | PFphB |  | supported | R
40128 | PFphC |  | supported | R
40130 | TotWhExp |  | supported | R
40132 | TotWhExpPhA |  | supported | R
40134 | TotWhExpPhB |  | supported | R
40136 | TotWhExpPhC |  | supported | R
40138 | TotWhImp |  | supported | R
40140 | TotWhImpPhA |  | supported | R
40142 | TotWhImpPhB |  | supported | R
40144 | TotWhImpPhC |  | supported | R
40146 | TotVAhExp |  | unimplemented | R
40148 | TotVAhExpPhA |  | unimplemented | R
40150 | TotVAhExpPhB |  | unimplemented | R
40152 | TotVAhExpPhC |  | unimplemented | R
40154 | TotVAhImp |  | supported | R
40156 | TotVAhImpPhA |  | unimplemented | R
40158 | TotVAhImpPhB |  | unimplemented | R
40160 | TotVAhImpPhC |  | unimplemented | R
40162 | TotVArhImpQ1 |  | supported | R
40164 | TotVArhImpQ1phA |  | unimplemented | R
40166 | TotVArhImpQ1phB |  | unimplemented | R
40168 | TotVArhImpQ1phC |  | unimplemented | R
40170 | TotVArhImpQ2 |  | supported | R
40172 | TotVArhImpQ2phA |  | unimplemented | R
40174 | TotVArhImpQ2phB |  | unimplemented | R
40176 | TotVArhImpQ2phC |  | unimplemented | R
40178 | TotVArhExpQ3 |  | supported | R
40180 | TotVArhExpQ3phA |  | unimplemented | R
40182 | TotVArhExpQ3phB |  | unimplemented | R
40184 | TotVArhExpQ3phC |  | unimplemented | R
40186 | TotVArhExpQ4 |  | supported | R
40188 | TotVArhExpQ4phA |  | unimplemented | R
40190 | TotVArhExpQ4phB |  | unimplemented | R
40192 | TotVArhExpQ4phC |  | unimplemented | R
40194 | Evt |  | supported | R
|  | M_EVENT_Power_Failure | supported
|  | M_EVENT_Under_Voltage | supported
|  | M_EVENT_Low_PF | supported
|  | M_EVENT_Over_Current | supported
|  | M_EVENT_Over_Voltage | supported
|  | M_EVENT_Missing_Sensor | supported
|  | M_EVENT_Reserved1 | supported
|  | M_EVENT_Reserved2 | supported
|  | M_EVENT_Reserved3 | supported
|  | M_EVENT_Reserved4 | supported
|  | M_EVENT_Reserved5 | supported
|  | M_EVENT_Reserved6 | supported
|  | M_EVENT_Reserved7 | supported
|  | M_EVENT_Reserved8 | supported
|  | M_EVENT_OEM01 | supported
|  | M_EVENT_OEM02 | supported
|  | M_EVENT_OEM03 | supported
|  | M_EVENT_OEM04 | supported
|  | M_EVENT_OEM05 | supported
|  | M_EVENT_OEM06 | supported
|  | M_EVENT_OEM07 | supported
|  | M_EVENT_OEM08 | supported
|  | M_EVENT_OEM09 | supported
|  | M_EVENT_OEM10 | supported
|  | M_EVENT_OEM11 | supported
|  | M_EVENT_OEM12 | supported
|  | M_EVENT_OEM13 | supported
|  | M_EVENT_OEM14 | supported
|  | M_EVENT_OEM15 | supported

## 214
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40070 | ID |  | 214 | R
40071 | L |  | 124 | R
40072 | A |  | supported | R
40074 | AphA |  | supported | R
40076 | AphB |  | supported | R
40078 | AphC |  | supported | R
40080 | PhV |  | unimplemented | R
40082 | PhVphA |  | unimplemented | R
40084 | PhVphB |  | unimplemented | R
40086 | PhVphC |  | unimplemented | R
40088 | PPV |  | supported | R
40090 | PPVphAB |  | supported | R
40092 | PPVphBC |  | supported | R
40094 | PPVphCA |  | supported | R
40096 | Hz |  | supported | R
40098 | W |  | supported | R
40100 | WphA |  | unimplemented | R
40102 | WphB |  | unimplemented | R
40104 | WphC |  | unimplemented | R
40106 | VA |  | supported | R
40108 | VAphA |  | unimplemented | R
40110 | VAphB |  | unimplemented | R
40112 | VAphC |  | unimplemented | R
40114 | VAR |  | supported | R
40116 | VARphA |  | unimplemented | R
40118 | VARphB |  | unimplemented | R
40120 | VARphC |  | unimplemented | R
40122 | PF |  | supported | R
40124 | PFphA |  | unimplemented | R
40126 | PFphB |  | unimplemented | R
40128 | PFphC |  | unimplemented | R
40130 | TotWhExp |  | supported | R
40132 | TotWhExpPhA |  | unimplemented | R
40134 | TotWhExpPhB |  | unimplemented | R
40136 | TotWhExpPhC |  | unimplemented | R
40138 | TotWhImp |  | supported | R
40140 | TotWhImpPhA |  | unimplemented | R
40142 | TotWhImpPhB |  | unimplemented | R
40144 | TotWhImpPhC |  | unimplemented | R
40146 | TotVAhExp |  | unimplemented | R
40148 | TotVAhExpPhA |  | unimplemented | R
40150 | TotVAhExpPhB |  | unimplemented | R
40152 | TotVAhExpPhC |  | unimplemented | R
40154 | TotVAhImp |  | supported | R
40156 | TotVAhImpPhA |  | unimplemented | R
40158 | TotVAhImpPhB |  | unimplemented | R
40160 | TotVAhImpPhC |  | unimplemented | R
40162 | TotVArhImpQ1 |  | supported | R
40164 | TotVArhImpQ1phA |  | unimplemented | R
40166 | TotVArhImpQ1phB |  | unimplemented | R
40168 | TotVArhImpQ1phC |  | unimplemented | R
40170 | TotVArhImpQ2 |  | supported | R
40172 | TotVArhImpQ2phA |  | unimplemented | R
40174 | TotVArhImpQ2phB |  | unimplemented | R
40176 | TotVArhImpQ2phC |  | unimplemented | R
40178 | TotVArhExpQ3 |  | supported | R
40180 | TotVArhExpQ3phA |  | unimplemented | R
40182 | TotVArhExpQ3phB |  | unimplemented | R
40184 | TotVArhExpQ3phC |  | unimplemented | R
40186 | TotVArhExpQ4 |  | supported | R
40188 | TotVArhExpQ4phA |  | unimplemented | R
40190 | TotVArhExpQ4phB |  | unimplemented | R
40192 | TotVArhExpQ4phC |  | unimplemented | R
40194 | Evt |  | supported | R
|  | M_EVENT_Power_Failure | supported
|  | M_EVENT_Under_Voltage | supported
|  | M_EVENT_Low_PF | supported
|  | M_EVENT_Over_Current | supported
|  | M_EVENT_Over_Voltage | supported
|  | M_EVENT_Missing_Sensor | supported
|  | M_EVENT_Reserved1 | supported
|  | M_EVENT_Reserved2 | supported
|  | M_EVENT_Reserved3 | supported
|  | M_EVENT_Reserved4 | supported
|  | M_EVENT_Reserved5 | supported
|  | M_EVENT_Reserved6 | supported
|  | M_EVENT_Reserved7 | supported
|  | M_EVENT_Reserved8 | supported
|  | M_EVENT_OEM01 | supported
|  | M_EVENT_OEM02 | supported
|  | M_EVENT_OEM03 | supported
|  | M_EVENT_OEM04 | supported
|  | M_EVENT_OEM05 | supported
|  | M_EVENT_OEM06 | supported
|  | M_EVENT_OEM07 | supported
|  | M_EVENT_OEM08 | supported
|  | M_EVENT_OEM09 | supported
|  | M_EVENT_OEM10 | supported
|  | M_EVENT_OEM11 | supported
|  | M_EVENT_OEM12 | supported
|  | M_EVENT_OEM13 | supported
|  | M_EVENT_OEM14 | supported
|  | M_EVENT_OEM15 | supported