## Instructions
SunSpec PICS
This SunSpec PICS was generated by SunSpec Dashboard v3.8.2 based on the model contents of the connected device.
Most of the necessary information is populated but the PICS must be completed before submission by performing the following steps:
1. Examine the entry in the 'Value' column for each point to verify correctness:
- Common model (1) points that are implemented should contain the current value.
- All other model points that are implemented and have a variable value should contain the string 'supported'.
- All other model points that are implemented and have a constant value should contain the constant value.
It is assumed that scale factors are constants. If they are not, change the value to 'supported'.
- All unimplemented points should contain the string 'unimplemented'.
- For each enumeration or bit field entry that is not implemented, change the string to 'unimplemented'.
2. Examine the 'R/W' column to ensure the access is correct. It should be either 'R' or 'RW'.
3. Some points require a value range be specified. Points that have a grey background in the Min and Max column must
have a minimum and maximum value specified in the Min and Max columns. The value should be the value with the scale
factor applied. For example, a value specified in these fields would be 97.34 not 9734 if the scale factor is -2.
For models that have repeating elements, the value range is specified on the points in the first element and are
applicable for all of the repeating elements.
4. For any point that has an implementation deviation or special considerations indicate the issue in the 'Conformance Notes' column.
The certificate number will be filled in when certification is complete and this file will be archived with the Testing Info tab removed
along with a copy of the certificate on sunspec.org.

## Product and Testing Info
Product Information
Product Type | Inverter
Manufacturer Name | Shanghai CHINT Power Systems Co., Ltd.
Product Name | Power Conversion System
Product Model Numbers | CPS ECB200KTL
Submitter Information
Full Name | Mr. Huan Cai
Job Title | Manager
Company Name | Shanghai CHINT Power Systems Co., Ltd.
Relationship to Manufacturer | Employee
Email | caihuan@chint.com
Phone | 17717616818
Device Under Test Information
Test Type | SunSpec Modbus Conformance Certification
Firmware Version Tested | 1.08.00
Firmware Checksum (in hex) | 28AEE412B083B61A9C2E22E562C3BCB7
Interface Type | RTU
If RTU
Interface Name | COM3
Unit ID | 1
Baud Rate | 9600
Parity | None
Timeout (secs) | 5
If Modbus TCP
IP Address
IP Port
Unit ID
If IEEE 2030.5
IP Address
IP Port
Poll Rate
Client PIN
Timeout (secs)
Reserved For SunSpec Alliance
SunSpec Certificate Number | SM-000057
Certificate Signer Name | Erin Mahan
Certificate Issued Date | 2026-06-22
Certificate Archive Location | https://sunspec.org/wp-content/uploads/2009/03/Chint_Modbus_Certificate_SM000057.pdf

## Test Lab Settings
Target Definition | Target Definition Label | Param | Param Label | Param Value

## IEEE 1547 Electrical Test Setup
Test Category | Param Definition | Param Definition Label | Param | Param Label | Param Unit | Param Value

## 1
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40002 | ID |  | 1 | R | 1 | 1
40003 | L |  | 66 | R
40004 | Mn |  | Chint Power | R
40020 | Md |  | CPS ECB200KTL | R
40036 | Opt |  | unimplemented | R
40044 | Vr |  | 1.07.00 | R
40052 | SN |  | 0281474976710656 | R
40068 | DA |  | supported | RW | 1 | 247
40069 | Pad |  | 32768 | R

## 701
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40070 | ID |  | 701 | R | 701 | 701
40071 | L |  | 153 | R
40072 | ACType |  | supported | R
|  | SINGLE_PHASE | supported
|  | SPLIT_PHASE | supported
|  | THREE_PHASE | supported
40073 | St |  | supported | R
|  | OFF | supported
|  | ON | supported
40074 | InvSt |  | supported | R
|  | OFF | supported
|  | SLEEPING | supported
|  | STARTING | supported
|  | RUNNING | supported
|  | THROTTLED | supported
|  | SHUTTING_DOWN | supported
|  | FAULT | supported
|  | STANDBY | supported
40075 | ConnSt |  | supported | R
|  | DISCONNECTED | supported
|  | CONNECTED | supported
40076 | Alrm |  | supported | R
|  | GROUND_FAULT | supported
|  | DC_OVER_VOLT | supported
|  | AC_DISCONNECT | supported
|  | DC_DISCONNECT | supported
|  | GRID_DISCONNECT | supported
|  | CABINET_OPEN | supported
|  | MANUAL_SHUTDOWN | supported
|  | OVER_TEMP | supported
|  | OVER_FREQUENCY | supported
|  | UNDER_FREQUENCY | supported
|  | AC_OVER_VOLT | supported
|  | AC_UNDER_VOLT | supported
|  | BLOWN_STRING_FUSE | supported
|  | UNDER_TEMP | supported
|  | MEMORY_LOSS | supported
|  | HW_TEST_FAILURE | supported
|  | MANUFACTURER_ALRM | supported
40078 | DERMode |  | unimplemented | R
|  | GRID_FOLLOWING | unimplemented
|  | GRID_FORMING | unimplemented
|  | PV_CLIPPED | unimplemented
40080 | W |  | supported | R
40081 | VA |  | supported | R
40082 | Var |  | supported | R
40083 | PF |  | supported | R
40084 | A |  | supported | R
40085 | LLV |  | supported | R
40086 | LNV |  | supported | R
40087 | Hz |  | supported | R
40089 | TotWhInj |  | supported | R
40093 | TotWhAbs |  | supported | R
40097 | TotVarhInj |  | unimplemented | R
40101 | TotVarhAbs |  | unimplemented | R
40105 | TmpAmb |  | supported | R
40106 | TmpCab |  | unimplemented | R
40107 | TmpSnk |  | unimplemented | R
40108 | TmpTrns |  | unimplemented | R
40109 | TmpSw |  | supported | R
40110 | TmpOt |  | unimplemented | R
40111 | WL1 |  | unimplemented | R
40112 | VAL1 |  | unimplemented | R
40113 | VarL1 |  | unimplemented | R
40114 | PFL1 |  | unimplemented | R
40115 | AL1 |  | supported | R
40116 | VL1L2 |  | unimplemented | R
40117 | VL1 |  | supported | R
40118 | TotWhInjL1 |  | unimplemented | R
40122 | TotWhAbsL1 |  | unimplemented | R
40126 | TotVarhInjL1 |  | unimplemented | R
40130 | TotVarhAbsL1 |  | unimplemented | R
40134 | WL2 |  | unimplemented | R
40135 | VAL2 |  | unimplemented | R
40136 | VarL2 |  | unimplemented | R
40137 | PFL2 |  | unimplemented | R
40138 | AL2 |  | supported | R
40139 | VL2L3 |  | unimplemented | R
40140 | VL2 |  | supported | R
40141 | TotWhInjL2 |  | unimplemented | R
40145 | TotWhAbsL2 |  | unimplemented | R
40149 | TotVarhInjL2 |  | unimplemented | R
40153 | TotVarhAbsL2 |  | unimplemented | R
40157 | WL3 |  | unimplemented | R
40158 | VAL3 |  | unimplemented | R
40159 | VarL3 |  | unimplemented | R
40160 | PFL3 |  | unimplemented | R
40161 | AL3 |  | supported | R
40162 | VL3L1 |  | unimplemented | R
40163 | VL3 |  | supported | R
40164 | TotWhInjL3 |  | unimplemented | R
40168 | TotWhAbsL3 |  | unimplemented | R
40172 | TotVarhInjL3 |  | unimplemented | R
40176 | TotVarhAbsL3 |  | unimplemented | R
40180 | ThrotPct |  | unimplemented | R
40181 | ThrotSrc |  | unimplemented | R
|  | MAX_W | unimplemented
|  | FIXED_W | unimplemented
|  | FIXED_VAR | unimplemented
|  | FIXED_PF | unimplemented
|  | VOLT_VAR | unimplemented
|  | FREQ_WATT | unimplemented
|  | DYN_REACT_CURR | unimplemented
|  | LVRT | unimplemented
|  | HVRT | unimplemented
|  | WATT_VAR | unimplemented
|  | VOLT_WATT | unimplemented
|  | SCHEDULED | unimplemented
|  | LFRT | unimplemented
|  | HFRT | unimplemented
|  | DERATED | unimplemented
40183 | A_SF |  | -2 | R
40184 | V_SF |  | -1 | R
40185 | Hz_SF |  | -2 | R
40186 | W_SF |  | 1 | R
40187 | PF_SF |  | -3 | R
40188 | VA_SF |  | 1 | R
40189 | Var_SF |  | 1 | R
40190 | TotWh_SF |  | 3 | R
40191 | TotVarh_SF |  | 3 | R
40192 | Tmp_SF |  | -1 | R
40193 | MnAlrmInfo |  | unimplemented | R

## 702
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40225 | ID |  | 702 | R | 702 | 702
40226 | L |  | 50 | R
40227 | WMaxRtg |  | 20000 | R
40228 | WOvrExtRtg |  | 16000 | R
40229 | WOvrExtRtgPF |  | 8 | R
40230 | WUndExtRtg |  | 16000 | R
40231 | WUndExtRtgPF |  | 8 | R
40232 | VAMaxRtg |  | 20000 | R
40233 | VarMaxInjRtg |  | 20000 | R
40234 | VarMaxAbsRtg |  | 20000 | R
40235 | WChaRteMaxRtg |  | 20000 | R
40236 | WDisChaRteMaxRtg |  | 20000 | R
40237 | VAChaRteMaxRtg |  | 20000 | R
40238 | VADisChaRteMaxRtg |  | 20000 | R
40239 | VNomRtg |  | 8000 | R
40240 | VMaxRtg |  | 8800 | R
40241 | VMinRtg |  | 7040 | R
40242 | AMaxRtg |  | 1 | R
40243 | PFOvrExtRtg |  | unimplemented | R
40244 | PFUndExtRtg |  | unimplemented | R
40245 | ReactSusceptRtg |  | 1 | R
40246 | NorOpCatRtg |  | 1 | R
|  | CAT_A | supported
|  | CAT_B | supported
40247 | AbnOpCatRtg |  | 2 | R
|  | CAT_1 | supported
|  | CAT_2 | supported
|  | CAT_3 | supported
40248 | CtrlModes |  | 14269 | R
|  | MAX_W | supported
|  | FIXED_W | supported
|  | FIXED_VAR | supported
|  | FIXED_PF | supported
|  | VOLT_VAR | supported
|  | FREQ_WATT | supported
|  | DYN_REACT_CURR | supported
|  | LV_TRIP | supported
|  | HV_TRIP | supported
|  | WATT_VAR | supported
|  | VOLT_WATT | supported
|  | SCHEDULED | supported
|  | LF_TRIP | supported
|  | HF_TRIP | supported
40250 | IntIslandCatRtg |  | 0 | R
|  | UNCATEGORIZED | supported
|  | INT_ISL_CAPABLE | supported
|  | BLACK_START_CAPABLE | supported
|  | ISOCH_CAPABLE | supported
40251 | WMax |  | unimplemented | RW
40252 | WMaxOvrExt |  | unimplemented | RW
40253 | WOvrExtPF |  | unimplemented | RW
40254 | WMaxUndExt |  | unimplemented | RW
40255 | WUndExtPF |  | unimplemented | RW
40256 | VAMax |  | unimplemented | RW
40257 | VarMaxInj |  | unimplemented | RW
40258 | VarMaxAbs |  | unimplemented | RW
40259 | WChaRteMax |  | unimplemented | RW
40260 | WDisChaRteMax |  | unimplemented | RW
40261 | VAChaRteMax |  | unimplemented | RW
40262 | VADisChaRteMax |  | unimplemented | RW
40263 | VNom |  | unimplemented | RW
40264 | VMax |  | unimplemented | RW
40265 | VMin |  | unimplemented | RW
40266 | AMax |  | unimplemented | RW
40267 | PFOvrExt |  | unimplemented | RW
40268 | PFUndExt |  | unimplemented | RW
40269 | IntIslandCat |  | unimplemented | RW
|  | UNCATEGORIZED | unimplemented
|  | INT_ISL_CAPABLE | unimplemented
|  | BLACK_START_CAPABLE | unimplemented
|  | ISOCH_CAPABLE | unimplemented
40270 | W_SF |  | 1 | R
40271 | PF_SF |  | -1 | R
40272 | VA_SF |  | 1 | R
40273 | Var_SF |  | 1 | R
40274 | V_SF |  | -1 | R
40275 | A_SF |  | 1 | R
40276 | S_SF |  | -1 | R

## 703
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40277 | ID |  | 703 | R | 703 | 703
40278 | L |  | 17 | R
40279 | ES |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40280 | ESVHi |  | supported | RW | 100 | 120
40281 | ESVLo |  | supported | RW | 50 | 100
40282 | ESHzHi |  | supported | RW | 50 | 52
40284 | ESHzLo |  | supported | RW | 47 | 50
40286 | ESDlyTms |  | supported | RW | 0 | 600
40288 | ESRndTms |  | unimplemented | RW
40290 | ESRmpTms |  | supported | RW | 1 | 1000
40292 | ESDlyRemTms |  | unimplemented | R
40294 | V_SF |  | -1 | R
40295 | Hz_SF |  | -2 | R

## 704
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40296 | ID |  | 704 | R | 704 | 704
40297 | L |  | 65 | R
40298 | PFWInjEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40299 | PFWInjEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40300 | PFWInjRvrtTms |  | unimplemented | RW
40302 | PFWInjRvrtRem |  | unimplemented | R
40304 | PFWAbsEna |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40305 | PFWAbsEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40306 | PFWAbsRvrtTms |  | unimplemented | RW
40308 | PFWAbsRvrtRem |  | unimplemented | R
40310 | WMaxLimPctEna |  | supported | RW
|  | DISABLED | unimplemented
|  | ENABLED | supported
40311 | WMaxLimPct |  | supported | RW | 0 | 100
40312 | WMaxLimPctRvrt |  | unimplemented | RW
40313 | WMaxLimPctEnaRvrt |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | unimplemented
40314 | WMaxLimPctRvrtTms |  | unimplemented | RW
40316 | WMaxLimPctRvrtRem |  | unimplemented | R
40318 | WSetEna |  | supported | RW
|  | DISABLED | unimplemented
|  | ENABLED | supported
40319 | WSetMod |  | supported | RW
|  | W_MAX_PCT | supported
|  | WATTS | unimplemented
40320 | WSet |  | unimplemented | RW
40322 | WSetRvrt |  | unimplemented | RW
40324 | WSetPct |  | supported | RW | -100 | 100
40325 | WSetPctRvrt |  | unimplemented | RW
40326 | WSetEnaRvrt |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | unimplemented
40327 | WSetRvrtTms |  | unimplemented | RW
40329 | WSetRvrtRem |  | unimplemented | R
40331 | VarSetEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40332 | VarSetMod |  | supported | RW
|  | W_MAX_PCT | unimplemented
|  | VAR_MAX_PCT | unimplemented
|  | VAR_AVAIL_PCT | unimplemented
|  | VA_MAX_PCT | supported
|  | VARS | unimplemented
40333 | VarSetPri |  | supported | RW
|  | ACTIVE | unimplemented
|  | REACTIVE | supported
|  | VENDOR | unimplemented
40334 | VarSet |  | unimplemented | RW
40336 | VarSetRvrt |  | unimplemented | RW
40338 | VarSetPct |  | supported | RW | -100 | 100
40339 | VarSetPctRvrt |  | unimplemented | RW
40340 | VarSetEnaRvrt |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | unimplemented
40341 | VarSetRvrtTms |  | unimplemented | RW
40343 | VarSetRvrtRem |  | unimplemented | R
40345 | WRmp |  | supported | RW | 10 | 10001
40346 | WRmpRef |  | supported | RW
|  | A_MAX | unimplemented
|  | W_MAX | supported
40347 | VarRmp |  | unimplemented | RW
40348 | AntiIslEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40349 | PF_SF |  | -3 | R
40350 | WMaxLimPct_SF |  | -3 | R
40351 | WSet_SF |  | 0 | R
40352 | WSetPct_SF |  | -1 | R
40353 | VarSet_SF |  | 2 | R
40354 | VarSetPct_SF |  | -1 | R
40355 | PFWInj.PF |  | supported | RW | 0.8 | 1
40356 | PFWInj.Ext |  | supported | RW
|  | OVER_EXCITED | supported
|  | UNDER_EXCITED | supported
40357 | PFWInjRvrt.PF |  | unimplemented | RW
40358 | PFWInjRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented
40359 | PFWAbs.PF |  | unimplemented | RW
40360 | PFWAbs.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented
40361 | PFWAbsRvrt.PF |  | unimplemented | RW
40362 | PFWAbsRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented