## Instructions
DER Security Corp
IEEE-1547 Protocol Information Conformance Statement (PICS)
For manufacturers of DER devices that must comply with IEEE 1547-2018 and UL 1741 SB.
This file was generated by SunSpec Dashboard or DER Security LabTest software. It is used to prepare and submit a product for testing at a Nationally Recognized Testing Lab (for electrical function validation and certification) or a SunSpec Authorized Testing laboratory (for SunSpec Modbus and/or IEEE 2030.5 communication protocol validation and certification). Some data is input by the user into the SunSpec Dashboard or DER Security LabTest software prior to autogenerating this spreadsheet and some data is read from Equipment Under Test (EUT) by SunSpec Dashboard or DER Security LabTest software after the spreadsheet is generated.
The Product and Testing Info tab contains general information about the unit under test, the manufacturer of the product, and the test laboratory network setup. It also contains an area for test laboratory personnel to enter information about an IEEE 1547 test that has previously been run on the unit under test.
The Test Lab Settings tab contains information about the testing laboratory and test engineer that ran a test. Data is input to this tab by the test engineer after a test run is completed.
The IEEE 1547 Electrical Test Setup tab contains information needed to configure the EUT for electrical testing according the IEEE 1547.1 standard. Most parameters are defined in the IEEE 1547.1 "Test Requirements" section (section 5.14.2) and some were by DER Security Corp to facilitate electrical test setup.
Numerical Tab names refer to the specific SunSpec Modbus models contained in the EUT and tab names that start with "2030.5 CSIP-" refer to specific IEEE 2030.5 capabilities of the product that the EUT will be evaluated against.
DER Security Corp License Agreement and Copyright
This document and the information contained herein is provided on an "AS IS" basis and the DER Security Corp DISCLAIMS ALL WARRANTIES, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY WARRANTY THAT THE USE OF THE INFORMATION HEREIN WILL NOT INFRINGE ANY OWNERSHIP RIGHTS OR ANY IMPLIED WARRANTIES OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE.
This document may be used, copied, and furnished to others, without restrictions of any kind, provided that this document itself may not be modified in anyway, except as needed by the DER Security Corp Technical Committee and as governed by the DER Security Corp IPR Policy. The complete policy of DER Security Corp can be found at https://www.dersec.io/.

## Product and Testing Info
Product Information
Product Type | Inverter
Manufacturer Name | DER Security
Product Name | DER Simulator
Product Model Numbers | 0000001
Submitter Information
Full Name | Jay Johnson
Job Title | CTO
Company Name | DER Security Corp
Relationship to Manufacturer | Employee
Email | jay@dersec.io
Phone
Device Under Test Information
Test Type | SunSpec Modbus for 1547
Firmware Version Tested | 3.8.2
Firmware Checksum (in hex) | 77317b115057f852ce4422f878b2adc3
Interface Type | Modbus TCP
If RTU
Interface Name
Unit ID
Baud Rate
Parity
Timeout (secs)
If Modbus TCP
IP Address | 127.0.0.1
IP Port | 502
Unit ID | 1
If IEEE 2030.5
IP Address
IP Port
Poll Rate
Client PIN
Timeout (secs)
SunSpec Certificate Number | SM-000046
Certificate Signer Name | Erin Mahan
Certificate Issued Date | 2025-09-19
Certificate Archive Location | https://sunspec.org/wp-content/uploads/2009/03/DERSec_Modbus-for-1547_Certificate_SM-000046-JJ.pdf

## Test Lab Settings
Target Definition | Target Definition Label | Param | Param Label | Param Value

## IEEE 1547 Electrical Test Setup
Test Category | Param Definition | Param Definition Label | Param | Param Label | Param Unit | Param Value

## 1
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40002 | ID |  | 1 | R | 1 | 1
40003 | L |  | 66 | R
40004 | Mn |  | DERSec | R
40020 | Md |  | DER Simulator | R
40036 | Opt |  | 10 kW DER | R
40044 | Vr |  | 1.2.3 | R
40052 | SN |  | SN-Three-Phase | R
40068 | DA |  | supported | RW | 0 | 247
40069 | Pad |  | 32768 | R

## 701
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40070 | ID |  | 701 | R | 701 | 701
40071 | L |  | 153 | R
40072 | ACType |  | supported | R
|  | SINGLE_PHASE | supported
|  | SPLIT_PHASE | supported
|  | THREE_PHASE | supported
40073 | St |  | supported | R
|  | OFF | supported
|  | ON | supported
40074 | InvSt |  | supported | R
|  | OFF | supported
|  | SLEEPING | supported
|  | STARTING | supported
|  | RUNNING | supported
|  | THROTTLED | supported
|  | SHUTTING_DOWN | supported
|  | FAULT | supported
|  | STANDBY | supported
40075 | ConnSt |  | supported | R
|  | DISCONNECTED | supported
|  | CONNECTED | supported
40076 | Alrm |  | supported | R
|  | GROUND_FAULT | supported
|  | DC_OVER_VOLT | supported
|  | AC_DISCONNECT | supported
|  | DC_DISCONNECT | supported
|  | GRID_DISCONNECT | supported
|  | CABINET_OPEN | supported
|  | MANUAL_SHUTDOWN | supported
|  | OVER_TEMP | supported
|  | OVER_FREQUENCY | supported
|  | UNDER_FREQUENCY | supported
|  | AC_OVER_VOLT | supported
|  | AC_UNDER_VOLT | supported
|  | BLOWN_STRING_FUSE | supported
|  | UNDER_TEMP | supported
|  | MEMORY_LOSS | supported
|  | HW_TEST_FAILURE | supported
|  | MANUFACTURER_ALRM | supported
40078 | DERMode |  | unimplemented | R
|  | GRID_FOLLOWING | unimplemented
|  | GRID_FORMING | unimplemented
|  | PV_CLIPPED | unimplemented
40080 | W |  | supported | R
40081 | VA |  | supported | R
40082 | Var |  | supported | R
40083 | PF |  | supported | R
40084 | A |  | supported | R
40085 | LLV |  | supported | R
40086 | LNV |  | supported | R
40087 | Hz |  | supported | R
40089 | TotWhInj |  | supported | R
40093 | TotWhAbs |  | supported | R
40097 | TotVarhInj |  | supported | R
40101 | TotVarhAbs |  | supported | R
40105 | TmpAmb |  | supported | R
40106 | TmpCab |  | supported | R
40107 | TmpSnk |  | supported | R
40108 | TmpTrns |  | supported | R
40109 | TmpSw |  | supported | R
40110 | TmpOt |  | supported | R
40111 | WL1 |  | supported | R
40112 | VAL1 |  | supported | R
40113 | VarL1 |  | supported | R
40114 | PFL1 |  | supported | R
40115 | AL1 |  | supported | R
40116 | VL1L2 |  | supported | R
40117 | VL1 |  | supported | R
40118 | TotWhInjL1 |  | supported | R
40122 | TotWhAbsL1 |  | supported | R
40126 | TotVarhInjL1 |  | supported | R
40130 | TotVarhAbsL1 |  | supported | R
40134 | WL2 |  | supported | R
40135 | VAL2 |  | supported | R
40136 | VarL2 |  | supported | R
40137 | PFL2 |  | supported | R
40138 | AL2 |  | supported | R
40139 | VL2L3 |  | supported | R
40140 | VL2 |  | supported | R
40141 | TotWhInjL2 |  | supported | R
40145 | TotWhAbsL2 |  | supported | R
40149 | TotVarhInjL2 |  | supported | R
40153 | TotVarhAbsL2 |  | supported | R
40157 | WL3 |  | supported | R
40158 | VAL3 |  | supported | R
40159 | VarL3 |  | supported | R
40160 | PFL3 |  | supported | R
40161 | AL3 |  | supported | R
40162 | VL3L1 |  | supported | R
40163 | VL3 |  | supported | R
40164 | TotWhInjL3 |  | supported | R
40168 | TotWhAbsL3 |  | supported | R
40172 | TotVarhInjL3 |  | supported | R
40176 | TotVarhAbsL3 |  | supported | R
40180 | ThrotPct |  | unimplemented | R
40181 | ThrotSrc |  | unimplemented | R
|  | MAX_W | unimplemented
|  | FIXED_W | unimplemented
|  | FIXED_VAR | unimplemented
|  | FIXED_PF | unimplemented
|  | VOLT_VAR | unimplemented
|  | FREQ_WATT | unimplemented
|  | DYN_REACT_CURR | unimplemented
|  | LVRT | unimplemented
|  | HVRT | unimplemented
|  | WATT_VAR | unimplemented
|  | VOLT_WATT | unimplemented
|  | SCHEDULED | unimplemented
|  | LFRT | unimplemented
|  | HFRT | unimplemented
|  | DERATED | unimplemented
40183 | A_SF |  | -1 | R
40184 | V_SF |  | -1 | R
40185 | Hz_SF |  | -3 | R
40186 | W_SF |  | 0 | R
40187 | PF_SF |  | -3 | R
40188 | VA_SF |  | 0 | R
40189 | Var_SF |  | 0 | R
40190 | TotWh_SF |  | 0 | R
40191 | TotVarh_SF |  | 0 | R
40192 | Tmp_SF |  | -1 | R
40193 | MnAlrmInfo |  | supported | R

## 702
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40225 | ID |  | 702 | R | 702 | 702
40226 | L |  | 50 | R
40227 | WMaxRtg |  | 10000 | R
40228 | WOvrExtRtg |  | 10000 | R
40229 | WOvrExtRtgPF |  | 800 | R
40230 | WUndExtRtg |  | 10000 | R
40231 | WUndExtRtgPF |  | 800 | R
40232 | VAMaxRtg |  | 10000 | R
40233 | VarMaxInjRtg |  | 4400 | R
40234 | VarMaxAbsRtg |  | 4400 | R
40235 | WChaRteMaxRtg |  | 0 | R
40236 | WDisChaRteMaxRtg |  | 0 | R
40237 | VAChaRteMaxRtg |  | 0 | R
40238 | VADisChaRteMaxRtg |  | 0 | R
40239 | VNomRtg |  | 4800 | R
40240 | VMaxRtg |  | 5760 | R
40241 | VMinRtg |  | 3840 | R
40242 | AMaxRtg |  | 150 | R
40243 | PFOvrExtRtg |  | 850 | R
40244 | PFUndExtRtg |  | 850 | R
40245 | ReactSusceptRtg |  | 0 | R
40246 | NorOpCatRtg |  | 1 | R
|  | CAT_A | supported
|  | CAT_B | supported
40247 | AbnOpCatRtg |  | 2 | R
|  | CAT_1 | supported
|  | CAT_2 | supported
|  | CAT_3 | supported
40248 | CtrlModes |  | 14271 | R
|  | MAX_W | supported
|  | FIXED_W | supported
|  | FIXED_VAR | supported
|  | FIXED_PF | supported
|  | VOLT_VAR | supported
|  | FREQ_WATT | supported
|  | DYN_REACT_CURR | supported
|  | LV_TRIP | supported
|  | HV_TRIP | supported
|  | WATT_VAR | supported
|  | VOLT_WATT | supported
|  | SCHEDULED | supported
|  | LF_TRIP | supported
|  | HF_TRIP | supported
40250 | IntIslandCatRtg |  | 0 | R
|  | UNCATEGORIZED | supported
|  | INT_ISL_CAPABLE | supported
|  | BLACK_START_CAPABLE | supported
|  | ISOCH_CAPABLE | supported
40251 | WMax |  | supported | RW | 0 | 10000
40252 | WMaxOvrExt |  | supported | RW | 0 | 10000
40253 | WOvrExtPF |  | supported | RW | 0.8 | 1
40254 | WMaxUndExt |  | supported | RW | 0 | 10000
40255 | WUndExtPF |  | supported | RW | 0.8 | 1
40256 | VAMax |  | supported | RW | 0 | 10000
40257 | VarMaxInj |  | supported | RW | 0 | 4400
40258 | VarMaxAbs |  | supported | RW | 0 | 4400
40259 | WChaRteMax |  | supported | RW | 0 | 0
40260 | WDisChaRteMax |  | supported | RW | 0 | 0
40261 | VAChaRteMax |  | supported | RW | 0 | 0
40262 | VADisChaRteMax |  | supported | RW | 0 | 0
40263 | VNom |  | supported | RW | 384 | 576
40264 | VMax |  | supported | RW | 384 | 576
40265 | VMin |  | supported | RW | 384 | 576
40266 | AMax |  | supported | RW | 0 | 15
40267 | PFOvrExt |  | unimplemented | RW
40268 | PFUndExt |  | unimplemented | RW
40269 | IntIslandCat |  | supported | RW | 0 | 0
|  | UNCATEGORIZED | supported
|  | INT_ISL_CAPABLE | supported
|  | BLACK_START_CAPABLE | supported
|  | ISOCH_CAPABLE | supported
40270 | W_SF |  | 0 | R
40271 | PF_SF |  | -3 | R
40272 | VA_SF |  | 0 | R
40273 | Var_SF |  | 0 | R
40274 | V_SF |  | -1 | R
40275 | A_SF |  | -1 | R
40276 | S_SF |  | -1 | R

## 703
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40277 | ID |  | 703 | R | 703 | 703
40278 | L |  | 17 | R
40279 | ES |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40280 | ESVHi |  | supported | RW | 105 | 106
40281 | ESVLo |  | supported | RW | 88 | 95
40282 | ESHzHi |  | supported | RW | 60.1 | 61
40284 | ESHzLo |  | supported | RW | 59 | 59.9
40286 | ESDlyTms |  | supported | RW | 0 | 600
40288 | ESRndTms |  | supported | RW | 0 | 1000
40290 | ESRmpTms |  | supported | RW | 1 | 1000
40292 | ESDlyRemTms |  | supported | R
40294 | V_SF |  | -1 | R
40295 | Hz_SF |  | -2 | R

## 704
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40296 | ID |  | 704 | R | 704 | 704
40297 | L |  | 65 | R
40298 | PFWInjEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40299 | PFWInjEnaRvrt |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40300 | PFWInjRvrtTms |  | supported | RW | 0 | 86400
40302 | PFWInjRvrtRem |  | supported | R
40304 | PFWAbsEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40305 | PFWAbsEnaRvrt |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40306 | PFWAbsRvrtTms |  | supported | RW | 0 | 86400
40308 | PFWAbsRvrtRem |  | supported | R
40310 | WMaxLimPctEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40311 | WMaxLimPct |  | supported | RW | 0 | 100
40312 | WMaxLimPctRvrt |  | supported | RW | 0 | 100
40313 | WMaxLimPctEnaRvrt |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40314 | WMaxLimPctRvrtTms |  | supported | RW | 0 | 86400
40316 | WMaxLimPctRvrtRem |  | supported | R
40318 | WSetEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40319 | WSetMod |  | supported | RW
|  | W_MAX_PCT | supported
|  | WATTS | supported
40320 | WSet |  | supported | RW | 0 | 10000
40322 | WSetRvrt |  | supported | RW | 0 | 10000
40324 | WSetPct |  | supported | RW | 0 | 100
40325 | WSetPctRvrt |  | supported | RW | 0 | 100
40326 | WSetEnaRvrt |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40327 | WSetRvrtTms |  | supported | RW | 0 | 86400
40329 | WSetRvrtRem |  | supported | R
40331 | VarSetEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40332 | VarSetMod |  | supported | RW
|  | W_MAX_PCT | supported
|  | VAR_MAX_PCT | supported
|  | VAR_AVAIL_PCT | supported
|  | VA_MAX_PCT | supported
|  | VARS | supported
40333 | VarSetPri |  | supported | RW
|  | ACTIVE | supported
|  | REACTIVE | supported
|  | VENDOR | supported
40334 | VarSet |  | supported | RW | -4400 | 4400
40336 | VarSetRvrt |  | supported | RW | -4400 | 4400
40338 | VarSetPct |  | supported | RW | -100 | 100
40339 | VarSetPctRvrt |  | supported | RW | -100 | 100
40340 | VarSetEnaRvrt |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40341 | VarSetRvrtTms |  | supported | RW | 0 | 86400
40343 | VarSetRvrtRem |  | supported | R
40345 | WRmp |  | supported | RW | 0 | 1000
40346 | WRmpRef |  | supported | RW
|  | A_MAX | supported
|  | W_MAX | supported
40347 | VarRmp |  | supported | RW | 0 | 1000
40348 | AntiIslEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40349 | PF_SF |  | -3 | R
40350 | WMaxLimPct_SF |  | -1 | R
40351 | WSet_SF |  | -1 | R
40352 | WSetPct_SF |  | -1 | R
40353 | VarSet_SF |  | -1 | R
40354 | VarSetPct_SF |  | -1 | R
40355 | PFWInj.PF |  | supported | RW | 0.85 | 1
40356 | PFWInj.Ext |  | supported | RW
|  | OVER_EXCITED | supported
|  | UNDER_EXCITED | supported
40357 | PFWInjRvrt.PF |  | supported | RW | 0.85 | 1
40358 | PFWInjRvrt.Ext |  | supported | RW
|  | OVER_EXCITED | supported
|  | UNDER_EXCITED | supported
40359 | PFWAbs.PF |  | unimplemented | RW
40360 | PFWAbs.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented
40361 | PFWAbsRvrt.PF |  | unimplemented | RW
40362 | PFWAbsRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented

## 705
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40363 | ID |  | 705 | R | 705 | 705
40364 | L |  | 67 | R
40365 | Ena |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40366 | AdptCrvReq |  | supported | RW
40367 | AdptCrvRslt |  | supported | R
|  | IN_PROGRESS | supported
|  | COMPLETED | supported
|  | FAILED | supported
40368 | NPt |  | 4 | R
40369 | NCrv |  | 3 | R
40370 | RvrtTms |  | supported | RW
40372 | RvrtRem |  | supported | R
40374 | RvrtCrv |  | supported | RW
40375 | V_SF |  | -2 | R
40376 | DeptRef_SF |  | -2 | R
40377 | RspTms_SF |  | -1 | R
40378 | Crv.1.ActPt |  | supported | RW | 4 | 4
40379 | Crv.1.DeptRef |  | supported | RW
|  | W_MAX_PCT | supported
|  | VAR_MAX_PCT | supported
|  | VAR_AVAL_PCT | supported
|  | VA_MAX_PCT | supported
40380 | Crv.1.Pri |  | supported | RW
|  | ACTIVE | supported
|  | REACTIVE | supported
|  | VENDOR | supported
40381 | Crv.1.VRef |  | supported | RW | 95 | 105
40382 | Crv.1.VRefAuto |  | supported | R
40383 | Crv.1.VRefAutoEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40384 | Crv.1.VRefAutoTms |  | supported | RW | 300 | 5000
40385 | Crv.1.RspTms |  | supported | RW | 1 | 90
40387 | Crv.1.ReadOnly |  | 1 | R
|  | RW | supported
|  | R | supported
40388 | Crv.1.Pt.1.V |  | supported | RW | 77 | 98
40389 | Crv.1.Pt.1.Var |  | supported | RW | 0 | 100
40390 | Crv.1.Pt.2.V |  | supported | RW | 97 | 100
40391 | Crv.1.Pt.2.Var |  | supported | RW | -100 | 100
40392 | Crv.1.Pt.3.V |  | supported | RW | 100 | 103
40393 | Crv.1.Pt.3.Var |  | supported | RW | -100 | 100
40394 | Crv.1.Pt.4.V |  | supported | RW | 102 | 118
40395 | Crv.1.Pt.4.Var |  | supported | RW | -100 | 0
40396 | Crv.2.ActPt |  | supported | RW
40397 | Crv.2.DeptRef |  | supported | RW
|  | W_MAX_PCT | supported
|  | VAR_MAX_PCT | supported
|  | VAR_AVAL_PCT | supported
|  | VA_MAX_PCT | supported
40398 | Crv.2.Pri |  | supported | RW
|  | ACTIVE | supported
|  | REACTIVE | supported
|  | VENDOR | supported
40399 | Crv.2.VRef |  | supported | RW
40400 | Crv.2.VRefAuto |  | supported | R
40401 | Crv.2.VRefAutoEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40402 | Crv.2.VRefAutoTms |  | supported | RW
40403 | Crv.2.RspTms |  | supported | RW
40405 | Crv.2.ReadOnly |  | 0 | R
|  | RW | supported
|  | R | supported
40406 | Crv.2.Pt.1.V |  | supported | RW
40407 | Crv.2.Pt.1.Var |  | supported | RW
40408 | Crv.2.Pt.2.V |  | supported | RW
40409 | Crv.2.Pt.2.Var |  | supported | RW
40410 | Crv.2.Pt.3.V |  | supported | RW
40411 | Crv.2.Pt.3.Var |  | supported | RW
40412 | Crv.2.Pt.4.V |  | supported | RW
40413 | Crv.2.Pt.4.Var |  | supported | RW
40414 | Crv.3.ActPt |  | supported | RW
40415 | Crv.3.DeptRef |  | supported | RW
|  | W_MAX_PCT | supported
|  | VAR_MAX_PCT | supported
|  | VAR_AVAL_PCT | supported
|  | VA_MAX_PCT | supported
40416 | Crv.3.Pri |  | supported | RW
|  | ACTIVE | supported
|  | REACTIVE | supported
|  | VENDOR | supported
40417 | Crv.3.VRef |  | supported | RW
40418 | Crv.3.VRefAuto |  | supported | R
40419 | Crv.3.VRefAutoEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40420 | Crv.3.VRefAutoTms |  | supported | RW
40421 | Crv.3.RspTms |  | supported | RW
40423 | Crv.3.ReadOnly |  | 0 | R
|  | RW | supported
|  | R | supported
40424 | Crv.3.Pt.1.V |  | supported | RW
40425 | Crv.3.Pt.1.Var |  | supported | RW
40426 | Crv.3.Pt.2.V |  | supported | RW
40427 | Crv.3.Pt.2.Var |  | supported | RW
40428 | Crv.3.Pt.3.V |  | supported | RW
40429 | Crv.3.Pt.3.Var |  | supported | RW
40430 | Crv.3.Pt.4.V |  | supported | RW
40431 | Crv.3.Pt.4.Var |  | supported | RW

## 706
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40432 | ID |  | 706 | R | 706 | 706
40433 | L |  | 40 | R
40434 | Ena |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40435 | AdptCrvReq |  | supported | RW
40436 | AdptCrvRslt |  | supported | R
|  | IN_PROGRESS | supported
|  | COMPLETED | supported
|  | FAILED | supported
40437 | NPt |  | 2 | R
40438 | NCrv |  | 3 | R
40439 | RvrtTms |  | supported | RW
40441 | RvrtRem |  | supported | R
40443 | RvrtCrv |  | supported | RW
40444 | V_SF |  | -1 | R
40445 | DeptRef_SF |  | -1 | R
40446 | RspTms_SF |  | -1 | R
40447 | Crv.1.ActPt |  | supported | RW | 2 | 2
40448 | Crv.1.DeptRef |  | supported | RW
|  | W_MAX_PCT | supported
|  | W_AVAL_PCT | supported
40449 | Crv.1.RspTms |  | supported | RW | 0.5 | 60
40451 | Crv.1.ReadOnly |  | 1 | R
|  | RW | supported
|  | R | supported
40452 | Crv.1.Pt.1.V |  | supported | RW | 105 | 109
40453 | Crv.1.Pt.1.W |  | supported | RW | 100 | 100
40454 | Crv.1.Pt.2.V |  | supported | RW | 106 | 110
40455 | Crv.1.Pt.2.W |  | supported | RW | 0 | 100
40456 | Crv.2.ActPt |  | supported | RW
40457 | Crv.2.DeptRef |  | supported | RW
|  | W_MAX_PCT | supported
|  | W_AVAL_PCT | supported
40458 | Crv.2.RspTms |  | supported | RW
40460 | Crv.2.ReadOnly |  | 0 | R
|  | RW | supported
|  | R | supported
40461 | Crv.2.Pt.1.V |  | supported | RW
40462 | Crv.2.Pt.1.W |  | supported | RW
40463 | Crv.2.Pt.2.V |  | supported | RW
40464 | Crv.2.Pt.2.W |  | supported | RW
40465 | Crv.3.ActPt |  | supported | RW
40466 | Crv.3.DeptRef |  | supported | RW
|  | W_MAX_PCT | supported
|  | W_AVAL_PCT | supported
40467 | Crv.3.RspTms |  | supported | RW
40469 | Crv.3.ReadOnly |  | 0 | R
|  | RW | supported
|  | R | supported
40470 | Crv.3.Pt.1.V |  | supported | RW
40471 | Crv.3.Pt.1.W |  | supported | RW
40472 | Crv.3.Pt.2.V |  | supported | RW
40473 | Crv.3.Pt.2.W |  | supported | RW

## 707
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40474 | ID |  | 707 | R | 707 | 707
40475 | L |  | 105 | R
40476 | Ena |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40477 | AdptCrvReq |  | supported | RW
40478 | AdptCrvRslt |  | supported | R
|  | IN_PROGRESS | supported
|  | COMPLETED | supported
|  | FAILED | supported
40479 | NPt |  | 5 | R
40480 | NCrvSet |  | 2 | R
40481 | V_SF |  | -1 | R
40482 | Tms_SF |  | -2 | R
40483 | Crv.1.ReadOnly |  | 1 | R
|  | RW | supported
|  | R | supported
40484 | Crv.1.MustTrip.ActPt |  | supported | RW | 5 | 5
40485 | Crv.1.MustTrip.Pt.1.V |  | supported | RW | 0 | 50
40486 | Crv.1.MustTrip.Pt.1.Tms |  | supported | RW | 2 | 21
40488 | Crv.1.MustTrip.Pt.2.V |  | supported | RW | 0 | 50
40489 | Crv.1.MustTrip.Pt.2.Tms |  | supported | RW | 2 | 21
40491 | Crv.1.MustTrip.Pt.3.V |  | supported | RW | 0 | 50
40492 | Crv.1.MustTrip.Pt.3.Tms |  | supported | RW | 21 | 50
40494 | Crv.1.MustTrip.Pt.4.V |  | supported | RW | 0 | 88
40495 | Crv.1.MustTrip.Pt.4.Tms |  | supported | RW | 21 | 50
40497 | Crv.1.MustTrip.Pt.5.V |  | supported | RW | 0 | 88
40498 | Crv.1.MustTrip.Pt.5.Tms |  | supported | RW | 50 | 55
40500 | Crv.1.MayTrip.ActPt |  | unimplemented | RW
40501 | Crv.1.MayTrip.Pt.1.V |  | unimplemented | RW
40502 | Crv.1.MayTrip.Pt.1.Tms |  | unimplemented | RW
40504 | Crv.1.MayTrip.Pt.2.V |  | unimplemented | RW
40505 | Crv.1.MayTrip.Pt.2.Tms |  | unimplemented | RW
40507 | Crv.1.MayTrip.Pt.3.V |  | unimplemented | RW
40508 | Crv.1.MayTrip.Pt.3.Tms |  | unimplemented | RW
40510 | Crv.1.MayTrip.Pt.4.V |  | unimplemented | RW
40511 | Crv.1.MayTrip.Pt.4.Tms |  | unimplemented | RW
40513 | Crv.1.MayTrip.Pt.5.V |  | unimplemented | RW
40514 | Crv.1.MayTrip.Pt.5.Tms |  | unimplemented | RW
40516 | Crv.1.MomCess.ActPt |  | supported | RW
40517 | Crv.1.MomCess.Pt.1.V |  | supported | RW
40518 | Crv.1.MomCess.Pt.1.Tms |  | supported | RW
40520 | Crv.1.MomCess.Pt.2.V |  | supported | RW
40521 | Crv.1.MomCess.Pt.2.Tms |  | supported | RW
40523 | Crv.1.MomCess.Pt.3.V |  | unimplemented | RW
40524 | Crv.1.MomCess.Pt.3.Tms |  | unimplemented | RW
40526 | Crv.1.MomCess.Pt.4.V |  | unimplemented | RW
40527 | Crv.1.MomCess.Pt.4.Tms |  | unimplemented | RW
40529 | Crv.1.MomCess.Pt.5.V |  | unimplemented | RW
40530 | Crv.1.MomCess.Pt.5.Tms |  | unimplemented | RW
40532 | Crv.2.ReadOnly |  | 0 | R
|  | RW | supported
|  | R | supported
40533 | Crv.2.MustTrip.ActPt |  | supported | RW
40534 | Crv.2.MustTrip.Pt.1.V |  | supported | RW
40535 | Crv.2.MustTrip.Pt.1.Tms |  | supported | RW
40537 | Crv.2.MustTrip.Pt.2.V |  | supported | RW
40538 | Crv.2.MustTrip.Pt.2.Tms |  | supported | RW
40540 | Crv.2.MustTrip.Pt.3.V |  | supported | RW
40541 | Crv.2.MustTrip.Pt.3.Tms |  | supported | RW
40543 | Crv.2.MustTrip.Pt.4.V |  | supported | RW
40544 | Crv.2.MustTrip.Pt.4.Tms |  | supported | RW
40546 | Crv.2.MustTrip.Pt.5.V |  | supported | RW
40547 | Crv.2.MustTrip.Pt.5.Tms |  | supported | RW
40549 | Crv.2.MayTrip.ActPt |  | unimplemented | RW
40550 | Crv.2.MayTrip.Pt.1.V |  | unimplemented | RW
40551 | Crv.2.MayTrip.Pt.1.Tms |  | unimplemented | RW
40553 | Crv.2.MayTrip.Pt.2.V |  | unimplemented | RW
40554 | Crv.2.MayTrip.Pt.2.Tms |  | unimplemented | RW
40556 | Crv.2.MayTrip.Pt.3.V |  | unimplemented | RW
40557 | Crv.2.MayTrip.Pt.3.Tms |  | unimplemented | RW
40559 | Crv.2.MayTrip.Pt.4.V |  | unimplemented | RW
40560 | Crv.2.MayTrip.Pt.4.Tms |  | unimplemented | RW
40562 | Crv.2.MayTrip.Pt.5.V |  | unimplemented | RW
40563 | Crv.2.MayTrip.Pt.5.Tms |  | unimplemented | RW
40565 | Crv.2.MomCess.ActPt |  | supported | RW
40566 | Crv.2.MomCess.Pt.1.V |  | supported | RW
40567 | Crv.2.MomCess.Pt.1.Tms |  | supported | RW
40569 | Crv.2.MomCess.Pt.2.V |  | supported | RW
40570 | Crv.2.MomCess.Pt.2.Tms |  | supported | RW
40572 | Crv.2.MomCess.Pt.3.V |  | unimplemented | RW
40573 | Crv.2.MomCess.Pt.3.Tms |  | unimplemented | RW
40575 | Crv.2.MomCess.Pt.4.V |  | unimplemented | RW
40576 | Crv.2.MomCess.Pt.4.Tms |  | unimplemented | RW
40578 | Crv.2.MomCess.Pt.5.V |  | unimplemented | RW
40579 | Crv.2.MomCess.Pt.5.Tms |  | unimplemented | RW

## 708
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40581 | ID |  | 708 | R | 708 | 708
40582 | L |  | 105 | R
40583 | Ena |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40584 | AdptCrvReq |  | supported | RW
40585 | AdptCrvRslt |  | supported | R
|  | IN_PROGRESS | supported
|  | COMPLETED | supported
|  | FAILED | supported
40586 | NPt |  | 5 | R
40587 | NCrvSet |  | 2 | R
40588 | V_SF |  | -1 | R
40589 | Tms_SF |  | -2 | R
40590 | Crv.1.ReadOnly |  | 1 | R
|  | RW | supported
|  | R | supported
40591 | Crv.1.MustTrip.ActPt |  | supported | RW | 5 | 5
40592 | Crv.1.MustTrip.Pt.1.V |  | supported | RW | 120 | 122
40593 | Crv.1.MustTrip.Pt.1.Tms |  | supported | RW | 0.16 | 0.16
40595 | Crv.1.MustTrip.Pt.2.V |  | supported | RW | 120 | 120
40596 | Crv.1.MustTrip.Pt.2.Tms |  | supported | RW | 0.16 | 0.16
40598 | Crv.1.MustTrip.Pt.3.V |  | supported | RW | 120 | 120
40599 | Crv.1.MustTrip.Pt.3.Tms |  | supported | RW | 1 | 13
40601 | Crv.1.MustTrip.Pt.4.V |  | supported | RW | 110 | 120
40602 | Crv.1.MustTrip.Pt.4.Tms |  | supported | RW | 1 | 13
40604 | Crv.1.MustTrip.Pt.5.V |  | supported | RW | 110 | 120
40605 | Crv.1.MustTrip.Pt.5.Tms |  | supported | RW | 14 | 15
40607 | Crv.1.MayTrip.ActPt |  | unimplemented | RW
40608 | Crv.1.MayTrip.Pt.1.V |  | unimplemented | RW
40609 | Crv.1.MayTrip.Pt.1.Tms |  | unimplemented | RW
40611 | Crv.1.MayTrip.Pt.2.V |  | unimplemented | RW
40612 | Crv.1.MayTrip.Pt.2.Tms |  | unimplemented | RW
40614 | Crv.1.MayTrip.Pt.3.V |  | unimplemented | RW
40615 | Crv.1.MayTrip.Pt.3.Tms |  | unimplemented | RW
40617 | Crv.1.MayTrip.Pt.4.V |  | unimplemented | RW
40618 | Crv.1.MayTrip.Pt.4.Tms |  | unimplemented | RW
40620 | Crv.1.MayTrip.Pt.5.V |  | unimplemented | RW
40621 | Crv.1.MayTrip.Pt.5.Tms |  | unimplemented | RW
40623 | Crv.1.MomCess.ActPt |  | supported | RW
40624 | Crv.1.MomCess.Pt.1.V |  | supported | RW
40625 | Crv.1.MomCess.Pt.1.Tms |  | supported | RW
40627 | Crv.1.MomCess.Pt.2.V |  | supported | RW
40628 | Crv.1.MomCess.Pt.2.Tms |  | supported | RW
40630 | Crv.1.MomCess.Pt.3.V |  | unimplemented | RW
40631 | Crv.1.MomCess.Pt.3.Tms |  | unimplemented | RW
40633 | Crv.1.MomCess.Pt.4.V |  | unimplemented | RW
40634 | Crv.1.MomCess.Pt.4.Tms |  | unimplemented | RW
40636 | Crv.1.MomCess.Pt.5.V |  | unimplemented | RW
40637 | Crv.1.MomCess.Pt.5.Tms |  | unimplemented | RW
40639 | Crv.2.ReadOnly |  | 0 | R
|  | RW | supported
|  | R | supported
40640 | Crv.2.MustTrip.ActPt |  | supported | RW
40641 | Crv.2.MustTrip.Pt.1.V |  | supported | RW
40642 | Crv.2.MustTrip.Pt.1.Tms |  | supported | RW
40644 | Crv.2.MustTrip.Pt.2.V |  | supported | RW
40645 | Crv.2.MustTrip.Pt.2.Tms |  | supported | RW
40647 | Crv.2.MustTrip.Pt.3.V |  | supported | RW
40648 | Crv.2.MustTrip.Pt.3.Tms |  | supported | RW
40650 | Crv.2.MustTrip.Pt.4.V |  | supported | RW
40651 | Crv.2.MustTrip.Pt.4.Tms |  | supported | RW
40653 | Crv.2.MustTrip.Pt.5.V |  | supported | RW
40654 | Crv.2.MustTrip.Pt.5.Tms |  | supported | RW
40656 | Crv.2.MayTrip.ActPt |  | unimplemented | RW
40657 | Crv.2.MayTrip.Pt.1.V |  | unimplemented | RW
40658 | Crv.2.MayTrip.Pt.1.Tms |  | unimplemented | RW
40660 | Crv.2.MayTrip.Pt.2.V |  | unimplemented | RW
40661 | Crv.2.MayTrip.Pt.2.Tms |  | unimplemented | RW
40663 | Crv.2.MayTrip.Pt.3.V |  | unimplemented | RW
40664 | Crv.2.MayTrip.Pt.3.Tms |  | unimplemented | RW
40666 | Crv.2.MayTrip.Pt.4.V |  | unimplemented | RW
40667 | Crv.2.MayTrip.Pt.4.Tms |  | unimplemented | RW
40669 | Crv.2.MayTrip.Pt.5.V |  | unimplemented | RW
40670 | Crv.2.MayTrip.Pt.5.Tms |  | unimplemented | RW
40672 | Crv.2.MomCess.ActPt |  | supported | RW
40673 | Crv.2.MomCess.Pt.1.V |  | supported | RW
40674 | Crv.2.MomCess.Pt.1.Tms |  | supported | RW
40676 | Crv.2.MomCess.Pt.2.V |  | supported | RW
40677 | Crv.2.MomCess.Pt.2.Tms |  | supported | RW
40679 | Crv.2.MomCess.Pt.3.V |  | unimplemented | RW
40680 | Crv.2.MomCess.Pt.3.Tms |  | unimplemented | RW
40682 | Crv.2.MomCess.Pt.4.V |  | unimplemented | RW
40683 | Crv.2.MomCess.Pt.4.Tms |  | unimplemented | RW
40685 | Crv.2.MomCess.Pt.5.V |  | unimplemented | RW
40686 | Crv.2.MomCess.Pt.5.Tms |  | unimplemented | RW

## 709
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40688 | ID |  | 709 | R | 709 | 709
40689 | L |  | 135 | R
40690 | Ena |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40691 | AdptCrvReq |  | supported | RW
40692 | AdptCrvRslt |  | supported | R
|  | IN_PROGRESS | supported
|  | COMPLETED | supported
|  | FAILED | supported
40693 | NPt |  | 5 | R
40694 | NCrvSet |  | 2 | R
40695 | Hz_SF |  | -1 | R
40696 | Tms_SF |  | -2 | R
40697 | Crv.1.ReadOnly |  | 1 | R
|  | RW | supported
|  | R | supported
40698 | Crv.1.MustTrip.ActPt |  | supported | RW | 5 | 5
40699 | Crv.1.MustTrip.Pt.1.Hz |  | supported | RW | 0 | 50
40701 | Crv.1.MustTrip.Pt.1.Tms |  | supported | RW | 0.16 | 1000
40703 | Crv.1.MustTrip.Pt.2.Hz |  | supported | RW | 50 | 57
40705 | Crv.1.MustTrip.Pt.2.Tms |  | supported | RW | 0.16 | 1000
40707 | Crv.1.MustTrip.Pt.3.Hz |  | supported | RW | 50 | 57
40709 | Crv.1.MustTrip.Pt.3.Tms |  | supported | RW | 180 | 1000
40711 | Crv.1.MustTrip.Pt.4.Hz |  | supported | RW | 50 | 59
40713 | Crv.1.MustTrip.Pt.4.Tms |  | supported | RW | 180 | 1000
40715 | Crv.1.MustTrip.Pt.5.Hz |  | supported | RW | 50 | 59
40717 | Crv.1.MustTrip.Pt.5.Tms |  | supported | RW | 180 | 1000
40719 | Crv.1.MayTrip.ActPt |  | unimplemented | RW
40720 | Crv.1.MayTrip.Pt.1.Hz |  | unimplemented | RW
40722 | Crv.1.MayTrip.Pt.1.Tms |  | unimplemented | RW
40724 | Crv.1.MayTrip.Pt.2.Hz |  | unimplemented | RW
40726 | Crv.1.MayTrip.Pt.2.Tms |  | unimplemented | RW
40728 | Crv.1.MayTrip.Pt.3.Hz |  | unimplemented | RW
40730 | Crv.1.MayTrip.Pt.3.Tms |  | unimplemented | RW
40732 | Crv.1.MayTrip.Pt.4.Hz |  | unimplemented | RW
40734 | Crv.1.MayTrip.Pt.4.Tms |  | unimplemented | RW
40736 | Crv.1.MayTrip.Pt.5.Hz |  | unimplemented | RW
40738 | Crv.1.MayTrip.Pt.5.Tms |  | unimplemented | RW
40740 | Crv.1.MomCess.ActPt |  | unimplemented | RW
40741 | Crv.1.MomCess.Pt.1.Hz |  | unimplemented | RW
40743 | Crv.1.MomCess.Pt.1.Tms |  | unimplemented | RW
40745 | Crv.1.MomCess.Pt.2.Hz |  | unimplemented | RW
40747 | Crv.1.MomCess.Pt.2.Tms |  | unimplemented | RW
40749 | Crv.1.MomCess.Pt.3.Hz |  | unimplemented | RW
40751 | Crv.1.MomCess.Pt.3.Tms |  | unimplemented | RW
40753 | Crv.1.MomCess.Pt.4.Hz |  | unimplemented | RW
40755 | Crv.1.MomCess.Pt.4.Tms |  | unimplemented | RW
40757 | Crv.1.MomCess.Pt.5.Hz |  | unimplemented | RW
40759 | Crv.1.MomCess.Pt.5.Tms |  | unimplemented | RW
40761 | Crv.2.ReadOnly |  | 0 | R
|  | RW | supported
|  | R | supported
40762 | Crv.2.MustTrip.ActPt |  | supported | RW
40763 | Crv.2.MustTrip.Pt.1.Hz |  | supported | RW
40765 | Crv.2.MustTrip.Pt.1.Tms |  | supported | RW
40767 | Crv.2.MustTrip.Pt.2.Hz |  | supported | RW
40769 | Crv.2.MustTrip.Pt.2.Tms |  | supported | RW
40771 | Crv.2.MustTrip.Pt.3.Hz |  | supported | RW
40773 | Crv.2.MustTrip.Pt.3.Tms |  | supported | RW
40775 | Crv.2.MustTrip.Pt.4.Hz |  | supported | RW
40777 | Crv.2.MustTrip.Pt.4.Tms |  | supported | RW
40779 | Crv.2.MustTrip.Pt.5.Hz |  | supported | RW
40781 | Crv.2.MustTrip.Pt.5.Tms |  | supported | RW
40783 | Crv.2.MayTrip.ActPt |  | unimplemented | RW
40784 | Crv.2.MayTrip.Pt.1.Hz |  | unimplemented | RW
40786 | Crv.2.MayTrip.Pt.1.Tms |  | unimplemented | RW
40788 | Crv.2.MayTrip.Pt.2.Hz |  | unimplemented | RW
40790 | Crv.2.MayTrip.Pt.2.Tms |  | unimplemented | RW
40792 | Crv.2.MayTrip.Pt.3.Hz |  | unimplemented | RW
40794 | Crv.2.MayTrip.Pt.3.Tms |  | unimplemented | RW
40796 | Crv.2.MayTrip.Pt.4.Hz |  | unimplemented | RW
40798 | Crv.2.MayTrip.Pt.4.Tms |  | unimplemented | RW
40800 | Crv.2.MayTrip.Pt.5.Hz |  | unimplemented | RW
40802 | Crv.2.MayTrip.Pt.5.Tms |  | unimplemented | RW
40804 | Crv.2.MomCess.ActPt |  | unimplemented | RW
40805 | Crv.2.MomCess.Pt.1.Hz |  | unimplemented | RW
40807 | Crv.2.MomCess.Pt.1.Tms |  | unimplemented | RW
40809 | Crv.2.MomCess.Pt.2.Hz |  | unimplemented | RW
40811 | Crv.2.MomCess.Pt.2.Tms |  | unimplemented | RW
40813 | Crv.2.MomCess.Pt.3.Hz |  | unimplemented | RW
40815 | Crv.2.MomCess.Pt.3.Tms |  | unimplemented | RW
40817 | Crv.2.MomCess.Pt.4.Hz |  | unimplemented | RW
40819 | Crv.2.MomCess.Pt.4.Tms |  | unimplemented | RW
40821 | Crv.2.MomCess.Pt.5.Hz |  | unimplemented | RW
40823 | Crv.2.MomCess.Pt.5.Tms |  | unimplemented | RW

## 710
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40825 | ID |  | 710 | R | 710 | 710
40826 | L |  | 135 | R
40827 | Ena |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40828 | AdptCrvReq |  | supported | RW
40829 | AdptCrvRslt |  | supported | R
|  | IN_PROGRESS | supported
|  | COMPLETED | supported
|  | FAILED | supported
40830 | NPt |  | 5 | R
40831 | NCrvSet |  | 2 | R
40832 | Hz_SF |  | -1 | R
40833 | Tms_SF |  | -2 | R
40834 | Crv.1.ReadOnly |  | 1 | R
|  | RW | supported
|  | R | supported
40835 | Crv.1.MustTrip.ActPt |  | supported | RW | 5 | 5
40836 | Crv.1.MustTrip.Pt.1.Hz |  | supported | RW | 62 | 67
40838 | Crv.1.MustTrip.Pt.1.Tms |  | supported | RW | 0.16 | 1000
40840 | Crv.1.MustTrip.Pt.2.Hz |  | supported | RW | 61.8 | 66
40842 | Crv.1.MustTrip.Pt.2.Tms |  | supported | RW | 0.16 | 1000
40844 | Crv.1.MustTrip.Pt.3.Hz |  | supported | RW | 61.8 | 66
40846 | Crv.1.MustTrip.Pt.3.Tms |  | supported | RW | 180 | 1000
40848 | Crv.1.MustTrip.Pt.4.Hz |  | supported | RW | 61 | 66
40850 | Crv.1.MustTrip.Pt.4.Tms |  | supported | RW | 180 | 1000
40852 | Crv.1.MustTrip.Pt.5.Hz |  | supported | RW | 61 | 66
40854 | Crv.1.MustTrip.Pt.5.Tms |  | supported | RW | 180 | 1000
40856 | Crv.1.MayTrip.ActPt |  | unimplemented | RW
40857 | Crv.1.MayTrip.Pt.1.Hz |  | unimplemented | RW
40859 | Crv.1.MayTrip.Pt.1.Tms |  | unimplemented | RW
40861 | Crv.1.MayTrip.Pt.2.Hz |  | unimplemented | RW
40863 | Crv.1.MayTrip.Pt.2.Tms |  | unimplemented | RW
40865 | Crv.1.MayTrip.Pt.3.Hz |  | unimplemented | RW
40867 | Crv.1.MayTrip.Pt.3.Tms |  | unimplemented | RW
40869 | Crv.1.MayTrip.Pt.4.Hz |  | unimplemented | RW
40871 | Crv.1.MayTrip.Pt.4.Tms |  | unimplemented | RW
40873 | Crv.1.MayTrip.Pt.5.Hz |  | unimplemented | RW
40875 | Crv.1.MayTrip.Pt.5.Tms |  | unimplemented | RW
40877 | Crv.1.MomCess.ActPt |  | unimplemented | RW
40878 | Crv.1.MomCess.Pt.1.Hz |  | unimplemented | RW
40880 | Crv.1.MomCess.Pt.1.Tms |  | unimplemented | RW
40882 | Crv.1.MomCess.Pt.2.Hz |  | unimplemented | RW
40884 | Crv.1.MomCess.Pt.2.Tms |  | unimplemented | RW
40886 | Crv.1.MomCess.Pt.3.Hz |  | unimplemented | RW
40888 | Crv.1.MomCess.Pt.3.Tms |  | unimplemented | RW
40890 | Crv.1.MomCess.Pt.4.Hz |  | unimplemented | RW
40892 | Crv.1.MomCess.Pt.4.Tms |  | unimplemented | RW
40894 | Crv.1.MomCess.Pt.5.Hz |  | unimplemented | RW
40896 | Crv.1.MomCess.Pt.5.Tms |  | unimplemented | RW
40898 | Crv.2.ReadOnly |  | 0 | R
|  | RW | supported
|  | R | supported
40899 | Crv.2.MustTrip.ActPt |  | supported | RW
40900 | Crv.2.MustTrip.Pt.1.Hz |  | supported | RW
40902 | Crv.2.MustTrip.Pt.1.Tms |  | supported | RW
40904 | Crv.2.MustTrip.Pt.2.Hz |  | supported | RW
40906 | Crv.2.MustTrip.Pt.2.Tms |  | supported | RW
40908 | Crv.2.MustTrip.Pt.3.Hz |  | supported | RW
40910 | Crv.2.MustTrip.Pt.3.Tms |  | supported | RW
40912 | Crv.2.MustTrip.Pt.4.Hz |  | supported | RW
40914 | Crv.2.MustTrip.Pt.4.Tms |  | supported | RW
40916 | Crv.2.MustTrip.Pt.5.Hz |  | supported | RW
40918 | Crv.2.MustTrip.Pt.5.Tms |  | supported | RW
40920 | Crv.2.MayTrip.ActPt |  | unimplemented | RW
40921 | Crv.2.MayTrip.Pt.1.Hz |  | unimplemented | RW
40923 | Crv.2.MayTrip.Pt.1.Tms |  | unimplemented | RW
40925 | Crv.2.MayTrip.Pt.2.Hz |  | unimplemented | RW
40927 | Crv.2.MayTrip.Pt.2.Tms |  | unimplemented | RW
40929 | Crv.2.MayTrip.Pt.3.Hz |  | unimplemented | RW
40931 | Crv.2.MayTrip.Pt.3.Tms |  | unimplemented | RW
40933 | Crv.2.MayTrip.Pt.4.Hz |  | unimplemented | RW
40935 | Crv.2.MayTrip.Pt.4.Tms |  | unimplemented | RW
40937 | Crv.2.MayTrip.Pt.5.Hz |  | unimplemented | RW
40939 | Crv.2.MayTrip.Pt.5.Tms |  | unimplemented | RW
40941 | Crv.2.MomCess.ActPt |  | unimplemented | RW
40942 | Crv.2.MomCess.Pt.1.Hz |  | unimplemented | RW
40944 | Crv.2.MomCess.Pt.1.Tms |  | unimplemented | RW
40946 | Crv.2.MomCess.Pt.2.Hz |  | unimplemented | RW
40948 | Crv.2.MomCess.Pt.2.Tms |  | unimplemented | RW
40950 | Crv.2.MomCess.Pt.3.Hz |  | unimplemented | RW
40952 | Crv.2.MomCess.Pt.3.Tms |  | unimplemented | RW
40954 | Crv.2.MomCess.Pt.4.Hz |  | unimplemented | RW
40956 | Crv.2.MomCess.Pt.4.Tms |  | unimplemented | RW
40958 | Crv.2.MomCess.Pt.5.Hz |  | unimplemented | RW
40960 | Crv.2.MomCess.Pt.5.Tms |  | unimplemented | RW

## 711
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40962 | ID |  | 711 | R | 711 | 711
40963 | L |  | 42 | R
40964 | Ena |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40965 | AdptCtlReq |  | supported | RW
40966 | AdptCtlRslt |  | supported | R
|  | IN_PROGRESS | supported
|  | COMPLETED | supported
|  | FAILED | supported
40967 | NCtl |  | 3 | R
40968 | RvrtTms |  | supported | RW
40970 | RvrtRem |  | supported | R
40972 | RvrtCtl |  | supported | RW
40973 | Db_SF |  | -3 | R
40974 | K_SF |  | -3 | R
40975 | RspTms_SF |  | -1 | R
40976 | Ctl.1.DbOf |  | supported | RW | 0.017 | 1
40978 | Ctl.1.DbUf |  | supported | RW | 0.017 | 1
40980 | Ctl.1.KOf |  | supported | RW | 0.02 | 0.05
40981 | Ctl.1.KUf |  | supported | RW | 0.02 | 0.05
40982 | Ctl.1.RspTms |  | supported | RW | 0.2 | 10
40984 | Ctl.1.PMin |  | supported | RW | -100 | 100
40985 | Ctl.1.ReadOnly |  | 1 | R
|  | RW | supported
|  | R | supported
40986 | Ctl.2.DbOf |  | supported | RW
40988 | Ctl.2.DbUf |  | supported | RW
40990 | Ctl.2.KOf |  | supported | RW
40991 | Ctl.2.KUf |  | supported | RW
40992 | Ctl.2.RspTms |  | supported | RW
40994 | Ctl.2.PMin |  | supported | RW
40995 | Ctl.2.ReadOnly |  | 0 | R
|  | RW | supported
|  | R | supported
40996 | Ctl.3.DbOf |  | supported | RW
40998 | Ctl.3.DbUf |  | supported | RW
41000 | Ctl.3.KOf |  | supported | RW
41001 | Ctl.3.KUf |  | supported | RW
41002 | Ctl.3.RspTms |  | supported | RW
41004 | Ctl.3.PMin |  | supported | RW
41005 | Ctl.3.ReadOnly |  | 0 | R
|  | RW | supported
|  | R | supported

## 712
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
41006 | ID |  | 712 | R | 712 | 712
41007 | L |  | 60 | R
41008 | Ena |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
41009 | AdptCrvReq |  | supported | RW
41010 | AdptCrvRslt |  | supported | R
|  | IN_PROGRESS | supported
|  | COMPLETED | supported
|  | FAILED | supported
41011 | NPt |  | 6 | R
41012 | NCrv |  | 3 | R
41013 | RvrtTms |  | supported | RW
41015 | RvrtRem |  | supported | R
41017 | RvrtCrv |  | supported | RW
41018 | W_SF |  | -1 | R
41019 | DeptRef_SF |  | -1 | R
41020 | Crv.1.ActPt |  | supported | RW | 6 | 6
41021 | Crv.1.DeptRef |  | supported | RW
|  | W_MAX_PCT | supported
|  | VAR_MAX_PCT | supported
|  | VAR_AVAL_PCT | supported
|  | VA_MAX_PCT | supported
41022 | Crv.1.Pri |  | supported | RW
|  | ACTIVE | supported
|  | REACTIVE | supported
41023 | Crv.1.ReadOnly |  | 1 | R
|  | RW | supported
|  | R | supported
41024 | Crv.1.Pt.1.W |  | supported | RW | -100 | -50
41025 | Crv.1.Pt.1.Var |  | supported | RW | -100 | 100
41026 | Crv.1.Pt.2.W |  | supported | RW | -80 | -40
41027 | Crv.1.Pt.2.Var |  | supported | RW | -100 | 100
41028 | Crv.1.Pt.3.W |  | supported | RW | -70 | 0
41029 | Crv.1.Pt.3.Var |  | supported | RW | -100 | 100
41030 | Crv.1.Pt.4.W |  | supported | RW | 0 | 70
41031 | Crv.1.Pt.4.Var |  | supported | RW | -100 | 100
41032 | Crv.1.Pt.5.W |  | supported | RW | 40 | 80
41033 | Crv.1.Pt.5.Var |  | supported | RW | -100 | 100
41034 | Crv.1.Pt.6.W |  | supported | RW | 50 | 100
41035 | Crv.1.Pt.6.Var |  | supported | RW | -100 | 100
41036 | Crv.2.ActPt |  | supported | RW
41037 | Crv.2.DeptRef |  | supported | RW
|  | W_MAX_PCT | supported
|  | VAR_MAX_PCT | supported
|  | VAR_AVAL_PCT | supported
|  | VA_MAX_PCT | supported
41038 | Crv.2.Pri |  | supported | RW
|  | ACTIVE | supported
|  | REACTIVE | supported
41039 | Crv.2.ReadOnly |  | 0 | R
|  | RW | supported
|  | R | supported
41040 | Crv.2.Pt.1.W |  | supported | RW
41041 | Crv.2.Pt.1.Var |  | supported | RW
41042 | Crv.2.Pt.2.W |  | supported | RW
41043 | Crv.2.Pt.2.Var |  | supported | RW
41044 | Crv.2.Pt.3.W |  | supported | RW
41045 | Crv.2.Pt.3.Var |  | supported | RW
41046 | Crv.2.Pt.4.W |  | supported | RW
41047 | Crv.2.Pt.4.Var |  | supported | RW
41048 | Crv.2.Pt.5.W |  | supported | RW
41049 | Crv.2.Pt.5.Var |  | supported | RW
41050 | Crv.2.Pt.6.W |  | supported | RW
41051 | Crv.2.Pt.6.Var |  | supported | RW
41052 | Crv.3.ActPt |  | supported | RW
41053 | Crv.3.DeptRef |  | supported | RW
|  | W_MAX_PCT | supported
|  | VAR_MAX_PCT | supported
|  | VAR_AVAL_PCT | supported
|  | VA_MAX_PCT | supported
41054 | Crv.3.Pri |  | supported | RW
|  | ACTIVE | supported
|  | REACTIVE | supported
41055 | Crv.3.ReadOnly |  | 0 | R
|  | RW | supported
|  | R | supported
41056 | Crv.3.Pt.1.W |  | supported | RW
41057 | Crv.3.Pt.1.Var |  | supported | RW
41058 | Crv.3.Pt.2.W |  | supported | RW
41059 | Crv.3.Pt.2.Var |  | supported | RW
41060 | Crv.3.Pt.3.W |  | supported | RW
41061 | Crv.3.Pt.3.Var |  | supported | RW
41062 | Crv.3.Pt.4.W |  | supported | RW
41063 | Crv.3.Pt.4.Var |  | supported | RW
41064 | Crv.3.Pt.5.W |  | supported | RW
41065 | Crv.3.Pt.5.Var |  | supported | RW
41066 | Crv.3.Pt.6.W |  | supported | RW
41067 | Crv.3.Pt.6.Var |  | supported | RW

## 714
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
41068 | ID |  | 714 | R | 714 | 714
41069 | L |  | 68 | R
41070 | PrtAlrms |  | supported | R
41072 | NPrt |  | 2 | R
41073 | DCA |  | supported | R
41074 | DCW |  | supported | R
41075 | DCWhInj |  | supported | R
41079 | DCWhAbs |  | supported | R
41083 | DCA_SF |  | -2 | R
41084 | DCV_SF |  | -1 | R
41085 | DCW_SF |  | 0 | R
41086 | DCWH_SF |  | 0 | R
41087 | Tmp_SF |  | -1 | R
41088 | Prt.1.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
41089 | Prt.1.ID |  | supported | R
41090 | Prt.1.IDStr |  | supported | R
41098 | Prt.1.DCA |  | supported | R
41099 | Prt.1.DCV |  | supported | R
41100 | Prt.1.DCW |  | supported | R
41101 | Prt.1.DCWhInj |  | supported | R
41105 | Prt.1.DCWhAbs |  | supported | R
41109 | Prt.1.Tmp |  | supported | R
41110 | Prt.1.DCSta |  | supported | R
|  | OFF | supported
|  | ON | supported
|  | WARNING | supported
|  | ERROR | supported
41111 | Prt.1.DCAlrm |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | INPUT_OVER_VOLTAGE | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | BLOWN_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | ARC_DETECTION | unimplemented
|  | RESERVED | unimplemented
|  | TEST_FAILED | unimplemented
|  | INPUT_UNDER_VOLTAGE | unimplemented
|  | INPUT_OVER_CURRENT | unimplemented
41113 | Prt.2.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
41114 | Prt.2.ID |  | supported | R
41115 | Prt.2.IDStr |  | supported | R
41123 | Prt.2.DCA |  | supported | R
41124 | Prt.2.DCV |  | supported | R
41125 | Prt.2.DCW |  | supported | R
41126 | Prt.2.DCWhInj |  | supported | R
41130 | Prt.2.DCWhAbs |  | supported | R
41134 | Prt.2.Tmp |  | supported | R
41135 | Prt.2.DCSta |  | supported | R
|  | OFF | supported
|  | ON | supported
|  | WARNING | supported
|  | ERROR | supported
41136 | Prt.2.DCAlrm |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | INPUT_OVER_VOLTAGE | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | BLOWN_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | ARC_DETECTION | unimplemented
|  | RESERVED | unimplemented
|  | TEST_FAILED | unimplemented
|  | INPUT_UNDER_VOLTAGE | unimplemented
|  | INPUT_OVER_CURRENT | unimplemented

## 64412
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
41138 | ID |  | 64412 | R
41139 | L |  | 43 | R
41140 | DAManipulation |  | supported | RW
|  | OFF | supported
|  | ON | supported
41141 | FalsifyDeviceIdentity |  | supported | RW
|  | OFF | supported
|  | ON | supported
41142 | MeasPAlwaysNameplate |  | supported | RW
|  | OFF | supported
|  | ON | supported
41143 | MeasQAlwaysMinimum |  | supported | RW
|  | OFF | supported
|  | ON | supported
41144 | MeasQAlwaysMaximum |  | supported | RW
|  | OFF | supported
|  | ON | supported
41145 | MeasQAlwaysZero |  | supported | RW
|  | OFF | supported
|  | ON | supported
41146 | MeasZeroP |  | supported | RW
|  | OFF | supported
|  | ON | supported
41147 | MeasInvertQ |  | supported | RW
|  | OFF | supported
|  | ON | supported
41148 | MeasLowV |  | supported | RW
|  | OFF | supported
|  | ON | supported
41149 | MeasHighV |  | supported | RW
|  | OFF | supported
|  | ON | supported
41150 | MeasLowL1V |  | supported | RW
|  | OFF | supported
|  | ON | supported
41151 | MeasHighL1V |  | supported | RW
|  | OFF | supported
|  | ON | supported
41152 | MeasLowF |  | supported | RW
|  | OFF | supported
|  | ON | supported
41153 | MeasHighF |  | supported | RW
|  | OFF | supported
|  | ON | supported
41154 | MeasLowAmps |  | supported | RW
|  | OFF | supported
|  | ON | supported
41155 | MeasHighAmps |  | supported | RW
|  | OFF | supported
|  | ON | supported
41156 | MeasHighS |  | supported | RW
|  | OFF | supported
|  | ON | supported
41157 | MeasLowS |  | supported | RW
|  | OFF | supported
|  | ON | supported
41158 | MeasHighQ |  | supported | RW
|  | OFF | supported
|  | ON | supported
41159 | MeasLowQ |  | supported | RW
|  | OFF | supported
|  | ON | supported
41160 | MeasLowPF |  | supported | RW
|  | OFF | supported
|  | ON | supported
41161 | MeasLowReversedPF |  | supported | RW
|  | OFF | supported
|  | ON | supported
41162 | NameplateHighP |  | supported | RW
|  | OFF | supported
|  | ON | supported
41163 | NameplateLowP |  | supported | RW
|  | OFF | supported
|  | ON | supported
41164 | NameplateHighS |  | supported | RW
|  | OFF | supported
|  | ON | supported
41165 | NameplateLowS |  | supported | RW
|  | OFF | supported
|  | ON | supported
41166 | NameplateHighQ |  | supported | RW
|  | OFF | supported
|  | ON | supported
41167 | NameplateLowQ |  | supported | RW
|  | OFF | supported
|  | ON | supported
41168 | NameplateHighNomV |  | supported | RW
|  | OFF | supported
|  | ON | supported
41169 | NameplateLowNomV |  | supported | RW
|  | OFF | supported
|  | ON | supported
41170 | NameplateLowAmps |  | supported | RW
|  | OFF | supported
|  | ON | supported
41171 | NameplateLowVarmaxinj |  | supported | RW
|  | OFF | supported
|  | ON | supported
41172 | NameplateLowVarmaxabs |  | supported | RW
|  | OFF | supported
|  | ON | supported
41173 | NameplateLowPF |  | supported | RW
|  | OFF | supported
|  | ON | supported
41174 | SettingsHighNomV |  | supported | RW
|  | OFF | supported
|  | ON | supported
41175 | SettingsLowAmps |  | supported | RW
|  | OFF | supported
|  | ON | supported
41176 | SettingsHighP |  | supported | RW
|  | OFF | supported
|  | ON | supported
41177 | SettingsLowP |  | supported | RW
|  | OFF | supported
|  | ON | supported
41178 | SettingsHighVAMax |  | supported | RW
|  | OFF | supported
|  | ON | supported
41179 | SettingsHighVarmaxinj |  | supported | RW
|  | OFF | supported
|  | ON | supported
41180 | SettingsHighVarmaxabs |  | supported | RW
|  | OFF | supported
|  | ON | supported
41181 | ChangeCommonModelID |  | supported | RW
|  | OFF | supported
|  | ON | supported
41182 | ChangeCommonModelLength |  | supported | RW
|  | OFF | supported
|  | ON | supported

## 64415
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
41183 | ID |  | 64415 | R
41184 | L |  | 3 | R
41185 | LogEventEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
41186 | HTTPMsg |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
41187 | COMM004Cert |  | supported | RW
|  | Default Certificate | supported
|  | COMM_004A | supported
|  | COMM_004B | supported
|  | COMM_004C | supported
|  | COMM_004D | supported
|  | COMM_004E | supported
|  | COMM_004F | supported
|  | COMM_004G | supported