## Instructions
SunSpec PICS Template
This SunSpec PICS template was generated by SunSpec Dashboard v1.0.6 based on the model contents of the connected device.
Most of the necessary information is populated but the PICS must be completed before submission by performing the following steps:
1. Examine the entry in the 'Value' column for each point to verify correctness:
- Common model (1) points that are implemented should contain the current value.
- All other model points that are implemented and have a variable value should contain the string 'supported'.
- All other model points that are implemented and have a constant value should contain the constant value.
It is assumed that scale factors are constants. If they are not, change the value to 'supported'.
- All unimplemented points should contain the string 'unimplemented'.
- For each enumeration or bit field entry that is not implemented, change the string to 'unimplemented'.
2. Examine the 'R/W' column to ensure the access is correct. It should be either 'R' or 'RW'.
3. For any point that has an implementation deviation or special considerations indicate the issue in the 'Conformance Notes' column.
The certificate number will be filled in when certification is complete and this file will be archived with the Testing Info tab removed
along with a copy of the certificate on sunspec.org.

## Certification Info
Certificate Number | SM-000007
Certificate Issue Date | August 19. 2020
Certificate Archive Link | https://sunspec.org/wp-content/uploads/2020/08/SunSpec-Deye-certificate-SM-000007.pdf
Date | 2020-08-19 08:38:50
Manufacturer Name | Deye
Product Name | SUN
Product Models | SUN-1-4K-G05P1-EU-AM1/CM1,SUN-3.6-6K-G05P1-EU-AM2/CM2,SUN-7-10K-G02P1-EU-AM2/CM2,SUN-18-25K-G05,SUN-18-36K-G04,SUN-40-60K-G04,SUN-60-80K-G04P3-EU-AM4,SUN-70-110K-G03,SUN-70-110K-G03P3-EU-BM6,SUN-120-136K-G01P3-EU-AM8/BM8,SUN-29.9-35K-G04P3-EU-DM2,SUN-40K-G04P3-EU-DM3,SUN-50K-G04P3-EU-DM4,SUN-8-25K-G06P3-EU-AM2/CM2,SUN-40-60K-G04P3-EU-CM4,SUN-18-36K-G04P3-EU-CM2,SUN-18-25K-G05P3-EU-CM2,SUN-3-15K-G06P3-EU-BM2/CM2-P1 SUN-3.6-10K-SG05LP1-EU-AM2-P,SUN-3.6-10K-SG05LP1-EU-SM2-P,AI-W5.1-3.6-10P1-EU-B,SUN-3-6K-SG04LP1,SUN-3.6-6K-SG04LP1-EU-SM2,SUN-3K-SG04LP1-24-EU,SUN-3K-SG04LP1-EU-SM1,SUN-3K-SG04LP1-24-EU-SM1,SUN-3.6-6K-SG06LP1-EU-BM2,SUN-3K-SG06LP1-24-EU-BM1,SUN-3K-SG06LP1-EU-BM1,SUN-7-12K-SG06LP1-EU-BM3,SUN-10-12K-SG02LP1-EU-AM3,SUN-10-12K-SG02LP1-EU-AM3-P,SUN-5-8K-SG02LP1-EU-AM2,SUN-7.6-8K-SG02LP1-EU-AM2-P, SUN-3-8K-SG06LP3-EU-BM2,SUN-3-12K-SG05LP3-EU-SM2,SUN-5-12K-SG01HP3-EU-DM2,SUN-10-25K-SG02HP3-EU-DM2,SUN-5-12K-SG04LP3-EU,SUN-5-12K-SG04LP3-EU-P,SUN-5-25K-SG01HP3-EU-AM2,SUN-12-18K-SG01LP1-EU-AM3-P,SUN-14-20K-SG05LP3-EU-SM2,SUN-14-20K-SG05LP3-EU-SM3-P,SUN-25-30K-SG02HP3-EU-AM3,SUN-29.9-35K-SG01HP3-EU-BM3,SUN-40-50K-SG01HP3-EU-BM4,SUN-29.9-35K-SG02HP3-EU-BM3,SUN-40-50K-SG02HP3-EU-BM4,SUN-29.9-35K-SG02HP3-EU-BM3-P,SUN-40-50K-SG02HP3-EU-BM4-P,SUN-60-80K-SG02HP3-EU-EM6,SUN-100-125K-SG02HP3-EU-GM10,SUN-100K-SG02HP3-EU-GM8,SUN-100-125K-PCS01HP3,SUN-100-125K-PCS01HP3-B, SUN-BK80-250-2.56KWH-EU-AM2/4-18/32L
Product Description | Solar Inverter
SunSpec Certificate Number | SM-000007
Certificate Signer Name | Erin Mahan
Certificate Issued Date | 2020-08-19
Certificate Archive Location | https://sunspec.org/wp-content/uploads/2009/03/Updated_Deye_Modbus_Certificate_SM000007.pdf

## Testing Info
Submitter | Chen Xudong
Email | chencxd@deye.com.cn
Phone | +8615067458497
Interface Type | RTU
Baud Rate | 9600
Slave Id | 1

## 1
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40002 | ID |  |  | 1
40003 | L |  |  | 66
40004 | Manufacturer (Mn) |  |  | Deye | R
40020 | Model (Md) |  |  | SUN-33K | R
40036 | Options (Opt) |  |  | unimplemented | R
40044 | Version (Vr) |  |  | 1864 | R
40052 | Serial Number (SN) |  |  | 0 | R
40068 | Device Address (DA) |  |  | 1 | RW
40069 | Pad |  |  |  | R

## 103
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40070 | ID |  |  | 103
40071 | L |  |  | 50
40072 | Amps (A) |  |  | supported | R
40073 | Amps PhaseA (AphA) |  |  | supported | R
40074 | Amps PhaseB (AphB) |  |  | supported | R
40075 | Amps PhaseC (AphC) |  |  | supported | R
40076 | A_SF |  |  | -1 | R
40077 | Phase Voltage AB (PPVphAB) |  |  | unimplemented | R
40078 | Phase Voltage BC (PPVphBC) |  |  | unimplemented | R
40079 | Phase Voltage CA (PPVphCA) |  |  | unimplemented | R
40080 | Phase Voltage AN (PhVphA) |  |  | supported | R
40081 | Phase Voltage BN (PhVphB) |  |  | supported | R
40082 | Phase Voltage CN (PhVphC) |  |  | supported | R
40083 | V_SF |  |  | -1 | R
40084 | Watts (W) |  |  | supported | R
40085 | W_SF |  |  | 1 | R
40086 | Hz |  |  | supported | R
40087 | Hz_SF |  |  | -2 | R
40088 | VA |  |  | unimplemented | R
40089 | VA_SF |  |  | unimplemented | R
40090 | VAr |  |  | unimplemented | R
40091 | VAr_SF |  |  | unimplemented | R
40092 | PF |  |  | unimplemented | R
40093 | PF_SF |  |  | unimplemented | R
40094 | WattHours (WH) |  |  | supported | R
40096 | WH_SF |  |  | 1 | R
40097 | DC Amps (DCA) |  |  | unimplemented | R
40098 | DCA_SF |  |  | unimplemented | R
40099 | DC Voltage (DCV) |  |  | unimplemented | R
40100 | DCV_SF |  |  | unimplemented | R
40101 | DC Watts (DCW) |  |  | unimplemented | R
40102 | DCW_SF |  |  | unimplemented | R
40103 | Cabinet Temperature (TmpCab) |  |  | supported | R
40104 | Heat Sink Temperature (TmpSnk) |  |  | unimplemented | R
40105 | Transformer Temperature (TmpTrns) |  |  | unimplemented | R
40106 | Other Temperature (TmpOt) |  |  | unimplemented | R
40107 | Tmp_SF |  |  | 0 | R
40108 | Operating State (St) |  |  | supported | R
|  |  | Off (OFF) | supported
|  |  | Sleeping (SLEEPING) | supported
|  |  | Starting (STARTING) | supported
|  |  | MPPT | supported
|  |  | Throttled (THROTTLED) | supported
|  |  | Shutting down (SHUTTING_DOWN) | supported
|  |  | Fault (FAULT) | supported
|  |  | Standby (STANDBY) | supported
40109 | Vendor Operating State (StVnd) |  |  | unimplemented | R
40110 | Event1 (Evt1) |  |  | supported | R
|  |  | Ground fault (GROUND_FAULT) | supported
|  |  | DC over voltage (DC_OVER_VOLT) | supported
|  |  | AC disconnect open (AC_DISCONNECT) | supported
|  |  | DC disconnect open (DC_DISCONNECT) | supported
|  |  | Grid shutdown (GRID_DISCONNECT) | supported
|  |  | Cabinet open (CABINET_OPEN) | supported
|  |  | Manual shutdown (MANUAL_SHUTDOWN) | supported
|  |  | Over temperature (OVER_TEMP) | supported
|  |  | Frequency above limit (OVER_FREQUENCY) | supported
|  |  | Frequency under limit (UNDER_FREQUENCY) | supported
|  |  | AC Voltage above limit (AC_OVER_VOLT) | supported
|  |  | AC Voltage under limit (AC_UNDER_VOLT) | supported
|  |  | Blown String fuse on input (BLOWN_STRING_FUSE) | supported
|  |  | Under temperature (UNDER_TEMP) | supported
|  |  | Generic Memory or Communication error (internal) (MEMORY_LOSS) | supported
|  |  | Hardware test failure (HW_TEST_FAILURE) | supported
40112 | Event Bitfield 2 (Evt2) |  |  | unimplemented | R
40114 | Vendor Event Bitfield 1 (EvtVnd1) |  |  | unimplemented | R
40116 | Vendor Event Bitfield 2 (EvtVnd2) |  |  | unimplemented | R
40118 | Vendor Event Bitfield 3 (EvtVnd3) |  |  | unimplemented | R
40120 | Vendor Event Bitfield 4 (EvtVnd4) |  |  | unimplemented | R

## 120
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40122 | ID |  |  | 120
40123 | L |  |  | 26
40124 | DERTyp |  |  | supported | R
|  |  | PV | supported
|  |  | PV_STOR | supported
40125 | WRtg |  |  | supported | R
40126 | WRtg_SF |  |  | 1 | R
40127 | VARtg |  |  | supported | R
40128 | VARtg_SF |  |  | 1 | R
40129 | VArRtgQ1 |  |  | supported | R
40130 | VArRtgQ2 |  |  | unimplemented | R
40131 | VArRtgQ3 |  |  | unimplemented | R
40132 | VArRtgQ4 |  |  | supported | R
40133 | VArRtg_SF |  |  | 1 | R
40134 | ARtg |  |  | supported | R
40135 | ARtg_SF |  |  | -1 | R
40136 | PFRtgQ1 |  |  | supported | R
40137 | PFRtgQ2 |  |  | unimplemented | R
40138 | PFRtgQ3 |  |  | unimplemented | R
40139 | PFRtgQ4 |  |  | supported | R
40140 | PFRtg_SF |  |  | -3 | R
40141 | WHRtg |  |  | unimplemented | R
40142 | WHRtg_SF |  |  | unimplemented | R
40143 | AhrRtg |  |  | unimplemented | R
40144 | AhrRtg_SF |  |  | unimplemented | R
40145 | MaxChaRte |  |  | unimplemented | R
40146 | MaxChaRte_SF |  |  | unimplemented | R
40147 | MaxDisChaRte |  |  | unimplemented | R
40148 | MaxDisChaRte_SF |  |  | unimplemented | R
40149 | Pad |  |  |  | R

## 121
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40150 | ID |  |  | 121
40151 | L |  |  | 30
40152 | WMax |  |  | supported | RW
40153 | VRef |  |  | supported | RW
40154 | VRefOfs |  |  | supported | RW
40155 | VMax |  |  | supported | RW
40156 | VMin |  |  | supported | RW
40157 | VAMax |  |  | supported | RW
40158 | VArMaxQ1 |  |  | unimplemented | RW
40159 | VArMaxQ2 |  |  | unimplemented | RW
40160 | VArMaxQ3 |  |  | unimplemented | RW
40161 | VArMaxQ4 |  |  | unimplemented | RW
40162 | WGra |  |  | supported | RW
40163 | PFMinQ1 |  |  | unimplemented | RW
40164 | PFMinQ2 |  |  | unimplemented | RW
40165 | PFMinQ3 |  |  | unimplemented | RW
40166 | PFMinQ4 |  |  | unimplemented | RW
40167 | VArAct |  |  | unimplemented | RW
|  |  | SWITCH | supported
|  |  | MAINTAIN | supported
40168 | ClcTotVA |  |  | unimplemented | RW
|  |  | VECTOR | supported
|  |  | ARITHMETIC | supported
40169 | MaxRmpRte |  |  | unimplemented | RW
40170 | ECPNomHz |  |  | unimplemented | RW
40171 | ConnPh |  |  | unimplemented | RW
|  |  | A | supported
|  |  | B | supported
|  |  | C | supported
40172 | WMax_SF |  |  | 1 | R
40173 | VRef_SF |  |  | -1 | R
40174 | VRefOfs_SF |  |  | -1 | R
40175 | VMinMax_SF |  |  | -1 | R
40176 | VAMax_SF |  |  | 1 | R
40177 | VArMax_SF |  |  | unimplemented | R
40178 | WGra_SF |  |  | -3 | R
40179 | PFMin_SF |  |  | unimplemented | R
40180 | MaxRmpRte_SF |  |  | unimplemented | R
40181 | ECPNomHz_SF |  |  | unimplemented | R

## 122
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40182 | ID |  |  | 122
40183 | L |  |  | 44
40184 | PVConn |  |  | supported | R
|  |  | CONNECTED | supported
|  |  | AVAILABLE | supported
|  |  | OPERATING | supported
|  |  | TEST | supported
40185 | StorConn |  |  | unimplemented | R
|  |  | CONNECTED | supported
|  |  | AVAILABLE | supported
|  |  | OPERATING | supported
|  |  | TEST | supported
40186 | ECPConn |  |  | supported | R
|  |  | CONNECTED | supported
40187 | ActWh |  |  | supported | R
40191 | ActVAh |  |  | unimplemented | R
40195 | ActVArhQ1 |  |  | unimplemented | R
40199 | ActVArhQ2 |  |  | unimplemented | R
40203 | ActVArhQ3 |  |  | unimplemented | R
40207 | ActVArhQ4 |  |  | unimplemented | R
40211 | VArAval |  |  | unimplemented | R
40212 | VArAval_SF |  |  | unimplemented | R
40213 | WAval |  |  | unimplemented | R
40214 | WAval_SF |  |  | unimplemented | R
40215 | StSetLimMsk |  |  | unimplemented | R
|  |  | WMax | supported
|  |  | VAMax | supported
|  |  | VArAval | supported
|  |  | VArMaxQ1 | supported
|  |  | VArMaxQ2 | supported
|  |  | VArMaxQ3 | supported
|  |  | VArMaxQ4 | supported
|  |  | PFMinQ1 | supported
|  |  | PFMinQ2 | supported
|  |  | PFMinQ3 | supported
|  |  | PFMinQ4 | supported
40217 | StActCtl |  |  | supported | R
|  |  | FixedW | supported
|  |  | FixedVAR | supported
|  |  | FixedPF | supported
|  |  | Volt-VAr | supported
|  |  | Freq-Watt-Param | supported
|  |  | Freq-Watt-Curve | supported
|  |  | Dyn-Reactive-Current | supported
|  |  | LVRT | supported
|  |  | HVRT | supported
|  |  | Watt-PF | supported
|  |  | Volt-Watt | supported
|  |  | Scheduled | supported
|  |  | LFRT | supported
|  |  | HFRT | supported
40219 | TmSrc |  |  | unimplemented | R
40223 | Tms |  |  | unimplemented | R
40225 | RtSt |  |  | supported | R
|  |  | LVRT_ACTIVE | supported
|  |  | HVRT_ACTIVE | supported
|  |  | LFRT_ACTIVE | supported
|  |  | HFRT_ACTIVE | supported
40226 | Ris |  |  | unimplemented | R
40227 | Ris_SF |  |  | unimplemented | R

## 123
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40228 | ID |  |  | 123
40229 | L |  |  | 24
40230 | Conn_WinTms |  |  | unimplemented | RW
40231 | Conn_RvrtTms |  |  | unimplemented | RW
40232 | Conn |  |  | supported | RW
|  |  | DISCONNECT | supported
|  |  | CONNECT | supported
40233 | WMaxLimPct |  |  | supported | RW
40234 | WMaxLimPct_WinTms |  |  | unimplemented | RW
40235 | WMaxLimPct_RvrtTms |  |  | unimplemented | RW
40236 | WMaxLimPct_RmpTms |  |  | unimplemented | RW
40237 | WMaxLim_Ena |  |  | supported | RW
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40238 | OutPFSet |  |  | supported | RW
40239 | OutPFSet_WinTms |  |  | unimplemented | RW
40240 | OutPFSet_RvrtTms |  |  | unimplemented | RW
40241 | OutPFSet_RmpTms |  |  | unimplemented | RW
40242 | OutPFSet_Ena |  |  | supported | RW
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40243 | VArWMaxPct |  |  | supported | RW
40244 | VArMaxPct |  |  | unimplemented | RW
40245 | VArAvalPct |  |  | unimplemented | RW
40246 | VArPct_WinTms |  |  | unimplemented | RW
40247 | VArPct_RvrtTms |  |  | unimplemented | RW
40248 | VArPct_RmpTms |  |  | unimplemented | RW
40249 | VArPct_Mod |  |  | supported | RW
|  |  | NONE | supported
|  |  | WMax | supported
|  |  | VArMax | supported
|  |  | VArAval | supported
40250 | VArPct_Ena |  |  | supported | RW
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40251 | WMaxLimPct_SF |  |  | -1 | R
40252 | OutPFSet_SF |  |  | -3 | R
40253 | VArPct_SF |  |  | -1 | R

## 126
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40254 | ID |  |  | 126
40255 | L |  |  | 64
40256 | ActCrv |  |  | supported | RW
40257 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40258 | WinTms |  |  | unimplemented | RW
40259 | RvrtTms |  |  | unimplemented | RW
40260 | RmpTms |  |  | unimplemented | RW
40261 | NCrv |  |  | supported | R
40262 | NPt |  |  | supported | R
40263 | V_SF |  |  | -2 | R
40264 | DeptRef_SF |  |  | -2 | R
40265 | RmpIncDec_SF |  |  | unimplemented | R
40266 | ActPt | 1 |  | supported | RW
40267 | DeptRef | 1 |  | supported | RW
|  |  | WMax | supported
|  |  | VArMax | supported
|  |  | VArAval | supported
40268 | V1 | 1 |  | supported | RW
40269 | VAr1 | 1 |  | supported | RW
40270 | V2 | 1 |  | supported | RW
40271 | VAr2 | 1 |  | supported | RW
40272 | V3 | 1 |  | supported | RW
40273 | VAr3 | 1 |  | supported | RW
40274 | V4 | 1 |  | supported | RW
40275 | VAr4 | 1 |  | supported | RW
40276 | V5 | 1 |  | supported | RW
40277 | VAr5 | 1 |  | supported | RW
40278 | V6 | 1 |  | supported | RW
40279 | VAr6 | 1 |  | supported | RW
40280 | V7 | 1 |  | supported | RW
40281 | VAr7 | 1 |  | supported | RW
40282 | V8 | 1 |  | supported | RW
40283 | VAr8 | 1 |  | supported | RW
40284 | V9 | 1 |  | supported | RW
40285 | VAr9 | 1 |  | supported | RW
40286 | V10 | 1 |  | supported | RW
40287 | VAr10 | 1 |  | supported | RW
40288 | V11 | 1 |  | supported | RW
40289 | VAr11 | 1 |  | supported | RW
40290 | V12 | 1 |  | supported | RW
40291 | VAr12 | 1 |  | supported | RW
40292 | V13 | 1 |  | supported | RW
40293 | VAr13 | 1 |  | supported | RW
40294 | V14 | 1 |  | supported | RW
40295 | VAr14 | 1 |  | supported | RW
40296 | V15 | 1 |  | supported | RW
40297 | VAr15 | 1 |  | supported | RW
40298 | V16 | 1 |  | supported | RW
40299 | VAr16 | 1 |  | supported | RW
40300 | V17 | 1 |  | supported | RW
40301 | VAr17 | 1 |  | supported | RW
40302 | V18 | 1 |  | supported | RW
40303 | VAr18 | 1 |  | supported | RW
40304 | V19 | 1 |  | supported | RW
40305 | VAr19 | 1 |  | supported | RW
40306 | V20 | 1 |  | supported | RW
40307 | VAr20 | 1 |  | supported | RW
40308 | CrvNam | 1 |  | unimplemented | RW
40316 | RmpTms | 1 |  | unimplemented | RW
40317 | RmpDecTmm | 1 |  | unimplemented | RW
40318 | RmpIncTmm | 1 |  | unimplemented | RW
40319 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported

## 127
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40320 | ID |  |  | 127
40321 | L |  |  | 10
40322 | WGra |  |  | supported | RW
40323 | HzStr |  |  | supported | RW
40324 | HzStop |  |  | supported | RW
40325 | HysEna |  |  | supported | RW
|  |  | ENABLED | supported
40326 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40327 | HzStopWGra |  |  | unimplemented | RW
40328 | WGra_SF |  |  | -2 | R
40329 | HzStrStop_SF |  |  | -2 | R
40330 | RmpIncDec_SF |  |  | unimplemented | R
40331 | Pad |  |  |  | R

## 128
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40332 | ID |  |  | 128
40333 | L |  |  | 14
40334 | ArGraMod |  |  | supported | RW
|  |  | EDGE | supported
|  |  | CENTER | supported
40335 | ArGraSag |  |  | supported | RW
40336 | ArGraSwell |  |  | supported | RW
40337 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40338 | FilTms |  |  | supported | RW
40339 | DbVMin |  |  | supported | RW
40340 | DbVMax |  |  | supported | RW
40341 | BlkZnV |  |  | unimplemented | RW
40342 | HysBlkZnV |  |  | unimplemented | RW
40343 | BlkZnTmms |  |  | unimplemented | RW
40344 | HoldTmms |  |  | supported | RW
40345 | ArGra_SF |  |  | -2 | R
40346 | VRefPct_SF |  |  | -1 | R
40347 | Pad |  |  |  | R

## 131
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40348 | ID |  |  | 131
40349 | L |  |  | 64
40350 | ActCrv |  |  | supported | RW
40351 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40352 | WinTms |  |  | unimplemented | RW
40353 | RvrtTms |  |  | unimplemented | RW
40354 | RmpTms |  |  | unimplemented | RW
40355 | NCrv |  |  | supported | R
40356 | NPt |  |  | supported | R
40357 | W_SF |  |  | -2 | R
40358 | PF_SF |  |  | -4 | R
40359 | RmpIncDec_SF |  |  | unimplemented | R
40360 | ActPt | 1 |  | supported | RW
40361 | W1 | 1 |  | supported | RW
40362 | PF1 | 1 |  | supported | RW
40363 | W2 | 1 |  | supported | RW
40364 | PF2 | 1 |  | supported | RW
40365 | W3 | 1 |  | supported | RW
40366 | PF3 | 1 |  | supported | RW
40367 | W4 | 1 |  | supported | RW
40368 | PF4 | 1 |  | supported | RW
40369 | W5 | 1 |  | supported | RW
40370 | PF5 | 1 |  | supported | RW
40371 | W6 | 1 |  | supported | RW
40372 | PF6 | 1 |  | supported | RW
40373 | W7 | 1 |  | supported | RW
40374 | PF7 | 1 |  | supported | RW
40375 | W8 | 1 |  | supported | RW
40376 | PF8 | 1 |  | supported | RW
40377 | W9 | 1 |  | supported | RW
40378 | PF9 | 1 |  | supported | RW
40379 | W10 | 1 |  | supported | RW
40380 | PF10 | 1 |  | supported | RW
40381 | W11 | 1 |  | supported | RW
40382 | PF11 | 1 |  | supported | RW
40383 | W12 | 1 |  | supported | RW
40384 | PF12 | 1 |  | supported | RW
40385 | W13 | 1 |  | supported | RW
40386 | PF13 | 1 |  | supported | RW
40387 | W14 | 1 |  | supported | RW
40388 | PF14 | 1 |  | supported | RW
40389 | W15 | 1 |  | supported | RW
40390 | PF15 | 1 |  | supported | RW
40391 | W16 | 1 |  | supported | RW
40392 | PF16 | 1 |  | supported | RW
40393 | W17 | 1 |  | supported | RW
40394 | PF17 | 1 |  | supported | RW
40395 | W18 | 1 |  | supported | RW
40396 | PF18 | 1 |  | supported | RW
40397 | W19 | 1 |  | supported | RW
40398 | PF19 | 1 |  | supported | RW
40399 | W20 | 1 |  | supported | RW
40400 | PF20 | 1 |  | supported | RW
40401 | CrvNam | 1 |  | unimplemented | RW
40409 | RmpPT1Tms | 1 |  | unimplemented | RW
40410 | RmpDecTmm | 1 |  | unimplemented | RW
40411 | RmpIncTmm | 1 |  | unimplemented | RW
40412 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
40413 | Pad | 1 |  |  | R

## 132
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40414 | ID |  |  | 132
40415 | L |  |  | 64
40416 | ActCrv |  |  | supported | RW
40417 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40418 | WinTms |  |  | unimplemented | RW
40419 | RvrtTms |  |  | unimplemented | RW
40420 | RmpTms |  |  | unimplemented | RW
40421 | NCrv |  |  | supported | R
40422 | NPt |  |  | supported | R
40423 | V_SF |  |  | -2 | R
40424 | DeptRef_SF |  |  | -2 | R
40425 | RmpIncDec_SF |  |  | unimplemented | R
40426 | ActPt | 1 |  | supported | RW
40427 | DeptRef | 1 |  | supported | RW
|  |  | %WMax | supported
|  |  | %WAval | supported
40428 | V1 | 1 |  | supported | RW
40429 | W1 | 1 |  | supported | RW
40430 | V2 | 1 |  | supported | RW
40431 | W2 | 1 |  | supported | RW
40432 | V3 | 1 |  | supported | RW
40433 | W3 | 1 |  | supported | RW
40434 | V4 | 1 |  | supported | RW
40435 | W4 | 1 |  | supported | RW
40436 | V5 | 1 |  | supported | RW
40437 | W5 | 1 |  | supported | RW
40438 | V6 | 1 |  | supported | RW
40439 | W6 | 1 |  | supported | RW
40440 | V7 | 1 |  | supported | RW
40441 | W7 | 1 |  | supported | RW
40442 | V8 | 1 |  | supported | RW
40443 | W8 | 1 |  | supported | RW
40444 | V9 | 1 |  | supported | RW
40445 | W9 | 1 |  | supported | RW
40446 | V10 | 1 |  | supported | RW
40447 | W10 | 1 |  | supported | RW
40448 | V11 | 1 |  | supported | RW
40449 | W11 | 1 |  | supported | RW
40450 | V12 | 1 |  | supported | RW
40451 | W12 | 1 |  | supported | RW
40452 | V13 | 1 |  | supported | RW
40453 | W13 | 1 |  | supported | RW
40454 | V14 | 1 |  | supported | RW
40455 | W14 | 1 |  | supported | RW
40456 | V15 | 1 |  | supported | RW
40457 | W15 | 1 |  | supported | RW
40458 | V16 | 1 |  | supported | RW
40459 | W16 | 1 |  | supported | RW
40460 | V17 | 1 |  | supported | RW
40461 | W17 | 1 |  | supported | RW
40462 | V18 | 1 |  | supported | RW
40463 | W18 | 1 |  | supported | RW
40464 | V19 | 1 |  | supported | RW
40465 | W19 | 1 |  | supported | RW
40466 | V20 | 1 |  | supported | RW
40467 | W20 | 1 |  | supported | RW
40468 | CrvNam | 1 |  | unimplemented | RW
40476 | RmpPt1Tms | 1 |  | unimplemented | RW
40477 | RmpDecTmm | 1 |  | unimplemented | RW
40478 | RmpIncTmm | 1 |  | unimplemented | RW
40479 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported