## Instructions
DER Security Corp
IEEE-1547 Protocol Information Conformance Statement (PICS)
For manufacturers of DER devices that must comply with IEEE 1547-2018 and UL 1741 SB.
This file was generated by SunSpec Dashboard or DER Security LabTest software. It is used to prepare and submit a product for testing at a Nationally Recognized Testing Lab (for electrical function validation and certification) or a SunSpec Authorized Testing laboratory (for SunSpec Modbus and/or IEEE 2030.5 communication protocol validation and certification). Some data is input by the user into the SunSpec Dashboard or DER Security LabTest software prior to autogenerating this spreadsheet and some data is read from Equipment Under Test (EUT) by SunSpec Dashboard or DER Security LabTest software after the spreadsheet is generated.
The Product and Testing Info tab contains general information about the unit under test, the manufacturer of the product, and the test laboratory network setup. It also contains an area for test laboratory personnel to enter information about an IEEE 1547 test that has previously been run on the unit under test.
The Test Lab Settings tab contains information about the testing laboratory and test engineer that ran a test. Data is input to this tab by the test engineer after a test run is completed.
The IEEE 1547 Electrical Test Setup tab contains information needed to configure the EUT for electrical testing according the IEEE 1547.1 standard. Most parameters are defined in the IEEE 1547.1 "Test Requirements" section (section 5.14.2) and some were by DER Security Corp to facilitate electrical test setup.
Numerical Tab names refer to the specific SunSpec Modbus models contained in the EUT and tab names that start with "2030.5 CSIP-" refer to specific IEEE 2030.5 capabilities of the product that the EUT will be evaluated against.
DER Security Corp License Agreement and Copyright
This document and the information contained herein is provided on an "AS IS" basis and the DER Security Corp DISCLAIMS ALL WARRANTIES, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY WARRANTY THAT THE USE OF THE INFORMATION HEREIN WILL NOT INFRINGE ANY OWNERSHIP RIGHTS OR ANY IMPLIED WARRANTIES OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE.
This document may be used, copied, and furnished to others, without restrictions of any kind, provided that this document itself may not be modified in anyway, except as needed by the DER Security Corp Technical Committee and as governed by the DER Security Corp IPR Policy. The complete policy of DER Security Corp can be found at https://www.dersec.io/.

## Product and Testing Info
Product Information
Product Type | Other
Manufacturer Name | EcoFlow Inc.
Product Name | EcoFlow OCEAN 2 Dongle
Product Model Numbers | EF HD-P3-WIFI-S2
Submitter Information
Full Name | Boyi Meng
Job Title | Certification Manager
Company Name | EcoFlow Inc.
Relationship to Manufacturer | Employee
Email | boyi.meng@ecoflow.com
Phone | +86 18913539557
Device Under Test Information
Test Type | SunSpec Modbus Conformance Certification
Firmware Version Tested | 1.0.0.0
Firmware Checksum (in hex) | 9cd2f9c5780a86dcc6b0f52668e0c1db
Interface Type | Modbus RTU and TCP
If RTU
Interface Name | RS485_2
Unit ID | 1
Baud Rate | 9600
Parity
Timeout (secs) | 1
If Modbus TCP
IP Address | 61.141.202.83
IP Port | 1502
Unit ID | 1
If IEEE 2030.5
IP Address
IP Port
Poll Rate
Client PIN
Timeout (secs)
Reserved For SunSpec Alliance
SunSpec Certificate Number | SM-000059
Certificate Signer Name | Dylan Tansy
Certificate Issued Date | 2026-07-02
Certificate Archive Location | https://sunspec.org/wp-content/uploads/2009/03/EcoFlow_SunSpec_Modbus_Certificate_SM000059.pdf

## Test Lab Settings
Target Definition | Target Definition Label | Param | Param Label | Param Value

## IEEE 1547 Electrical Test Setup
Test Category | Param Definition | Param Definition Label | Param | Param Label | Param Unit | Param Value

## 1
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40002 | ID |  | 1 | R | 1 | 1
40003 | L |  | 66 | R
40004 | Mn |  | EcoFlow | R
40020 | Md |  | RE001-EMS | R
40036 | Opt |  | unimplemented | R
40044 | Vr |  | 1.0.0.0 | R
40052 | SN |  | RE11ZE1AVHAV0014 | R
40068 | DA |  | supported | RW | 0 | 247
40069 | Pad |  | 0 | R

## 701
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40070 | ID |  | 701 | R | 701 | 701
40071 | L |  | 153 | R
40072 | ACType |  | supported | R
|  | SINGLE_PHASE | supported
|  | SPLIT_PHASE | supported
|  | THREE_PHASE | supported
40073 | St |  | supported | R
|  | OFF | supported
|  | ON | supported
40074 | InvSt |  | supported | R
|  | OFF | supported
|  | SLEEPING | supported
|  | STARTING | supported
|  | RUNNING | supported
|  | THROTTLED | supported
|  | SHUTTING_DOWN | supported
|  | FAULT | supported
|  | STANDBY | supported
40075 | ConnSt |  | unimplemented | R
|  | DISCONNECTED | unimplemented
|  | CONNECTED | unimplemented
40076 | Alrm |  | supported | R
|  | GROUND_FAULT | supported
|  | DC_OVER_VOLT | supported
|  | AC_DISCONNECT | supported
|  | DC_DISCONNECT | supported
|  | GRID_DISCONNECT | supported
|  | CABINET_OPEN | supported
|  | MANUAL_SHUTDOWN | supported
|  | OVER_TEMP | supported
|  | OVER_FREQUENCY | supported
|  | UNDER_FREQUENCY | supported
|  | AC_OVER_VOLT | supported
|  | AC_UNDER_VOLT | supported
|  | BLOWN_STRING_FUSE | supported
|  | UNDER_TEMP | supported
|  | MEMORY_LOSS | supported
|  | HW_TEST_FAILURE | supported
|  | MANUFACTURER_ALRM | supported
40078 | DERMode |  | unimplemented | R
|  | GRID_FOLLOWING | unimplemented
|  | GRID_FORMING | unimplemented
|  | PV_CLIPPED | unimplemented
40080 | W |  | supported | R
40081 | VA |  | supported | R
40082 | Var |  | supported | R
40083 | PF |  | supported | R
40084 | A |  | supported | R
40085 | LLV |  | unimplemented | R
40086 | LNV |  | unimplemented | R
40087 | Hz |  | supported | R
40089 | TotWhInj |  | supported | R
40093 | TotWhAbs |  | unimplemented | R
40097 | TotVarhInj |  | unimplemented | R
40101 | TotVarhAbs |  | unimplemented | R
40105 | TmpAmb |  | unimplemented | R
40106 | TmpCab |  | supported | R
40107 | TmpSnk |  | unimplemented | R
40108 | TmpTrns |  | unimplemented | R
40109 | TmpSw |  | unimplemented | R
40110 | TmpOt |  | unimplemented | R
40111 | WL1 |  | unimplemented | R
40112 | VAL1 |  | unimplemented | R
40113 | VarL1 |  | unimplemented | R
40114 | PFL1 |  | unimplemented | R
40115 | AL1 |  | supported | R
40116 | VL1L2 |  | supported | R
40117 | VL1 |  | supported | R
40118 | TotWhInjL1 |  | unimplemented | R
40122 | TotWhAbsL1 |  | unimplemented | R
40126 | TotVarhInjL1 |  | unimplemented | R
40130 | TotVarhAbsL1 |  | unimplemented | R
40134 | WL2 |  | unimplemented | R
40135 | VAL2 |  | unimplemented | R
40136 | VarL2 |  | unimplemented | R
40137 | PFL2 |  | unimplemented | R
40138 | AL2 |  | supported | R
40139 | VL2L3 |  | supported | R
40140 | VL2 |  | supported | R
40141 | TotWhInjL2 |  | unimplemented | R
40145 | TotWhAbsL2 |  | unimplemented | R
40149 | TotVarhInjL2 |  | unimplemented | R
40153 | TotVarhAbsL2 |  | unimplemented | R
40157 | WL3 |  | unimplemented | R
40158 | VAL3 |  | unimplemented | R
40159 | VarL3 |  | unimplemented | R
40160 | PFL3 |  | unimplemented | R
40161 | AL3 |  | supported | R
40162 | VL3L1 |  | supported | R
40163 | VL3 |  | supported | R
40164 | TotWhInjL3 |  | unimplemented | R
40168 | TotWhAbsL3 |  | unimplemented | R
40172 | TotVarhInjL3 |  | unimplemented | R
40176 | TotVarhAbsL3 |  | unimplemented | R
40180 | ThrotPct |  | unimplemented | R
40181 | ThrotSrc |  | unimplemented | R
|  | MAX_W | unimplemented
|  | FIXED_W | unimplemented
|  | FIXED_VAR | unimplemented
|  | FIXED_PF | unimplemented
|  | VOLT_VAR | unimplemented
|  | FREQ_WATT | unimplemented
|  | DYN_REACT_CURR | unimplemented
|  | LVRT | unimplemented
|  | HVRT | unimplemented
|  | WATT_VAR | unimplemented
|  | VOLT_WATT | unimplemented
|  | SCHEDULED | unimplemented
|  | LFRT | unimplemented
|  | HFRT | unimplemented
|  | DERATED | unimplemented
40183 | A_SF |  | -2 | R
40184 | V_SF |  | 0 | R
40185 | Hz_SF |  | -2 | R
40186 | W_SF |  | 0 | R
40187 | PF_SF |  | -2 | R
40188 | VA_SF |  | 0 | R
40189 | Var_SF |  | 0 | R
40190 | TotWh_SF |  | 0 | R
40191 | TotVarh_SF |  | unimplemented | R
40192 | Tmp_SF |  | 0 | R
40193 | MnAlrmInfo |  | unimplemented | R

## 702
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40225 | ID |  | 702 | R | 702 | 702
40226 | L |  | 50 | R
40227 | WMaxRtg |  | 10000 | R
40228 | WOvrExtRtg |  | unimplemented | R
40229 | WOvrExtRtgPF |  | unimplemented | R
40230 | WUndExtRtg |  | unimplemented | R
40231 | WUndExtRtgPF |  | unimplemented | R
40232 | VAMaxRtg |  | 10000 | R
40233 | VarMaxInjRtg |  | unimplemented | R
40234 | VarMaxAbsRtg |  | unimplemented | R
40235 | WChaRteMaxRtg |  | unimplemented | R
40236 | WDisChaRteMaxRtg |  | unimplemented | R
40237 | VAChaRteMaxRtg |  | unimplemented | R
40238 | VADisChaRteMaxRtg |  | unimplemented | R
40239 | VNomRtg |  | 400 | R
40240 | VMaxRtg |  | unimplemented | R
40241 | VMinRtg |  | unimplemented | R
40242 | AMaxRtg |  | 2500 | R
40243 | PFOvrExtRtg |  | unimplemented | R
40244 | PFUndExtRtg |  | unimplemented | R
40245 | ReactSusceptRtg |  | unimplemented | R
40246 | NorOpCatRtg |  | unimplemented | R
|  | CAT_A | unimplemented
|  | CAT_B | unimplemented
40247 | AbnOpCatRtg |  | unimplemented | R
|  | CAT_1 | unimplemented
|  | CAT_2 | unimplemented
|  | CAT_3 | unimplemented
40248 | CtrlModes |  | unimplemented | R
|  | MAX_W | unimplemented
|  | FIXED_W | unimplemented
|  | FIXED_VAR | unimplemented
|  | FIXED_PF | unimplemented
|  | VOLT_VAR | unimplemented
|  | FREQ_WATT | unimplemented
|  | DYN_REACT_CURR | unimplemented
|  | LV_TRIP | unimplemented
|  | HV_TRIP | unimplemented
|  | WATT_VAR | unimplemented
|  | VOLT_WATT | unimplemented
|  | SCHEDULED | unimplemented
|  | LF_TRIP | unimplemented
|  | HF_TRIP | unimplemented
40250 | IntIslandCatRtg |  | unimplemented | R
|  | UNCATEGORIZED | unimplemented
|  | INT_ISL_CAPABLE | unimplemented
|  | BLACK_START_CAPABLE | unimplemented
|  | ISOCH_CAPABLE | unimplemented
40251 | WMax |  | unimplemented | RW
40252 | WMaxOvrExt |  | unimplemented | RW
40253 | WOvrExtPF |  | unimplemented | RW
40254 | WMaxUndExt |  | unimplemented | RW
40255 | WUndExtPF |  | unimplemented | RW
40256 | VAMax |  | unimplemented | RW
40257 | VarMaxInj |  | unimplemented | RW
40258 | VarMaxAbs |  | unimplemented | RW
40259 | WChaRteMax |  | unimplemented | RW
40260 | WDisChaRteMax |  | unimplemented | RW
40261 | VAChaRteMax |  | unimplemented | RW
40262 | VADisChaRteMax |  | unimplemented | RW
40263 | VNom |  | unimplemented | RW
40264 | VMax |  | unimplemented | RW
40265 | VMin |  | unimplemented | RW
40266 | AMax |  | unimplemented | RW
40267 | PFOvrExt |  | unimplemented | RW
40268 | PFUndExt |  | unimplemented | RW
40269 | IntIslandCat |  | unimplemented | RW
|  | UNCATEGORIZED | unimplemented
|  | INT_ISL_CAPABLE | unimplemented
|  | BLACK_START_CAPABLE | unimplemented
|  | ISOCH_CAPABLE | unimplemented
40270 | W_SF |  | 0 | R
40271 | PF_SF |  | unimplemented | R
40272 | VA_SF |  | 0 | R
40273 | Var_SF |  | unimplemented | R
40274 | V_SF |  | 0 | R
40275 | A_SF |  | -2 | R
40276 | S_SF |  | 0 | R

## 703
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40277 | ID |  | 703 | R | 703 | 703
40278 | L |  | 17 | R
40279 | ES |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40280 | ESVHi |  | unimplemented | RW
40281 | ESVLo |  | unimplemented | RW
40282 | ESHzHi |  | unimplemented | RW
40284 | ESHzLo |  | unimplemented | RW
40286 | ESDlyTms |  | unimplemented | RW
40288 | ESRndTms |  | unimplemented | RW
40290 | ESRmpTms |  | unimplemented | RW
40292 | ESDlyRemTms |  | unimplemented | R
40294 | V_SF |  | unimplemented | R
40295 | Hz_SF |  | unimplemented | R

## 704
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40296 | ID |  | 704 | R | 704 | 704
40297 | L |  | 65 | R
40298 | PFWInjEna |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40299 | PFWInjEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40300 | PFWInjRvrtTms |  | unimplemented | RW
40302 | PFWInjRvrtRem |  | unimplemented | R
40304 | PFWAbsEna |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40305 | PFWAbsEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40306 | PFWAbsRvrtTms |  | unimplemented | RW
40308 | PFWAbsRvrtRem |  | unimplemented | R
40310 | WMaxLimPctEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40311 | WMaxLimPct |  | supported | RW | 0 | 100
40312 | WMaxLimPctRvrt |  | unimplemented | RW
40313 | WMaxLimPctEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40314 | WMaxLimPctRvrtTms |  | unimplemented | RW
40316 | WMaxLimPctRvrtRem |  | unimplemented | R
40318 | WSetEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40319 | WSetMod |  | supported | RW
|  | W_MAX_PCT | supported
|  | WATTS | supported
40320 | WSet |  | supported | RW | 0 | 10000
40322 | WSetRvrt |  | unimplemented | RW
40324 | WSetPct |  | supported | RW | 0 | 100
40325 | WSetPctRvrt |  | unimplemented | RW
40326 | WSetEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40327 | WSetRvrtTms |  | unimplemented | RW
40329 | WSetRvrtRem |  | unimplemented | R
40331 | VarSetEna |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40332 | VarSetMod |  | unimplemented | RW
|  | W_MAX_PCT | unimplemented
|  | VAR_MAX_PCT | unimplemented
|  | VAR_AVAIL_PCT | unimplemented
|  | VA_MAX_PCT | unimplemented
|  | VARS | unimplemented
40333 | VarSetPri |  | unimplemented | RW
|  | ACTIVE | unimplemented
|  | REACTIVE | unimplemented
|  | VENDOR | unimplemented
40334 | VarSet |  | unimplemented | RW
40336 | VarSetRvrt |  | unimplemented | RW
40338 | VarSetPct |  | unimplemented | RW
40339 | VarSetPctRvrt |  | unimplemented | RW
40340 | VarSetEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40341 | VarSetRvrtTms |  | unimplemented | RW
40343 | VarSetRvrtRem |  | unimplemented | R
40345 | WRmp |  | unimplemented | RW
40346 | WRmpRef |  | unimplemented | RW
|  | A_MAX | unimplemented
|  | W_MAX | unimplemented
40347 | VarRmp |  | unimplemented | RW
40348 | AntiIslEna |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40349 | PF_SF |  | unimplemented | R
40350 | WMaxLimPct_SF |  | 0 | R
40351 | WSet_SF |  | 0 | R
40352 | WSetPct_SF |  | 0 | R
40353 | VarSet_SF |  | 0 | R
40354 | VarSetPct_SF |  | 0 | R
40355 | PFWInj.PF |  | unimplemented | RW
40356 | PFWInj.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented
40357 | PFWInjRvrt.PF |  | unimplemented | RW
40358 | PFWInjRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented
40359 | PFWAbs.PF |  | unimplemented | RW
40360 | PFWAbs.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented
40361 | PFWAbsRvrt.PF |  | unimplemented | RW
40362 | PFWAbsRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented

## 714
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40363 | ID |  | 714 | R | 714 | 714
40364 | L |  | 43 | R
40365 | PrtAlrms |  | unimplemented | R
40367 | NPrt |  | 1 | R
40368 | DCA |  | supported | R
40369 | DCW |  | supported | R
40370 | DCWhInj |  | supported | R
40374 | DCWhAbs |  | supported | R
40378 | DCA_SF |  | -2 | R
40379 | DCV_SF |  | 0 | R
40380 | DCW_SF |  | 0 | R
40381 | DCWH_SF |  | unimplemented | R
40382 | Tmp_SF |  | unimplemented | R
40383 | Prt.1.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
40384 | Prt.1.ID |  | supported | R
40385 | Prt.1.IDStr |  | unimplemented | R
40393 | Prt.1.DCA |  | unimplemented | R
40394 | Prt.1.DCV |  | unimplemented | R
40395 | Prt.1.DCW |  | unimplemented | R
40396 | Prt.1.DCWhInj |  | supported | R
40400 | Prt.1.DCWhAbs |  | supported | R
40404 | Prt.1.Tmp |  | unimplemented | R
40405 | Prt.1.DCSta |  | unimplemented | R
|  | OFF | unimplemented
|  | ON | unimplemented
|  | WARNING | unimplemented
|  | ERROR | unimplemented
40406 | Prt.1.DCAlrm |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | INPUT_OVER_VOLTAGE | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | BLOWN_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | ARC_DETECTION | unimplemented
|  | RESERVED | unimplemented
|  | TEST_FAILED | unimplemented
|  | INPUT_UNDER_VOLTAGE | unimplemented
|  | INPUT_OVER_CURRENT | unimplemented

## 715
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40408 | ID |  | 715 | R
40409 | L |  | 7 | R
40410 | LocRemCtl |  | supported | R
|  | REMOTE | supported
|  | LOCAL | supported
40411 | DERHb |  | supported | R
40413 | ControllerHb |  | supported | RW | 0 | 4294967294
40415 | AlarmReset |  | supported | RW | 0 | 1
40416 | OpCtl |  | supported | RW
|  | STOP | supported
|  | START | supported
|  | ENTER_STANDBY | supported
|  | EXIT_STANDBY | supported