## Instructions
SunSpec PICS
This SunSpec PICS was generated by SunSpec Dashboard v3.8.2 based on the model contents of the connected device.
Most of the necessary information is populated but the PICS must be completed before submission by performing the following steps:
1. Examine the entry in the 'Value' column for each point to verify correctness:
- Common model (1) points that are implemented should contain the current value.
- All other model points that are implemented and have a variable value should contain the string 'supported'.
- All other model points that are implemented and have a constant value should contain the constant value.
It is assumed that scale factors are constants. If they are not, change the value to 'supported'.
- All unimplemented points should contain the string 'unimplemented'.
- For each enumeration or bit field entry that is not implemented, change the string to 'unimplemented'.
2. Examine the 'R/W' column to ensure the access is correct. It should be either 'R' or 'RW'.
3. Some points require a value range be specified. Points that have a grey background in the Min and Max column must
have a minimum and maximum value specified in the Min and Max columns. The value should be the value with the scale
factor applied. For example, a value specified in these fields would be 97.34 not 9734 if the scale factor is -2.
For models that have repeating elements, the value range is specified on the points in the first element and are
applicable for all of the repeating elements.
4. For any point that has an implementation deviation or special considerations indicate the issue in the 'Conformance Notes' column.
The certificate number will be filled in when certification is complete and this file will be archived with the Testing Info tab removed
along with a copy of the certificate on sunspec.org.

## Product and Testing Info
Product Information
Product Type | Inverter
Manufacturer Name | Ginlong Technologies Co., Ltd.
Product Name | Solis Inverter
Product Model Numbers | S6-GR3P3K02-NV-ND S6-GR3P4K02-NV-ND S6-GR3P5K02-NV-ND S6-GR3P6K02-NV-ND S6-GR3P8K02-NV-ND S6-GR3P9K02-NV-ND S6-GR3P10K02-NV-ND S6-GR3P5K02-LV-ND S6-GR3P6K02-LV-ND S5-GR3P5K-AU S5-GR3P6K-AU S5-GR3P8K-AU S5-GR3P9K-AU S5-GR3P10K-AU S5-GR3P3K S5-GR3P4K S5-GR3P5K S5-GR3P5K-LV S5-GR3P6K S5-GR3P6K-LV S5-GR3P8K S5-GR3P8K-BE S5-GR3P9K S5-GR3P10K S5-GR3P10K-LV S5-GR3P10K-LV-BE S5-GR3P10K-BE S5-GR3P13K S5-GR3P12K S5-GR3P15K S5-GR3P17K S5-GR3P20K S5-GR3P3K(21A) S5-GR3P4K(21A) S5-GR3P5K(21A) S5-GR3P6K(21A) S5-GR3P8K(21A) S5-GR3P9K(21A) S5-GR3P10K(21A) S5-GR3P12K(21A) S5-GR3P15K(21A) S5-GR3P17K(21A) S5-GR3P20K(21A) S5-GR3P25K(21A) S5-GR3P5K-LV(21A) S5-GR3P6K-LV(21A) S5-GR3P10K-LV(21A) S5-GR3P12K-LV(21A) S5-GR3P15K-LV(21A) S5-GR3P12K-AU(21A) S5-GR3P15K-AU(21A) S5-GR3P17K-AU(21A) S5-GR3P20K-AU(21A) S6-GR3P5K03-NV-ND-AU S6-GR3P6K03-NV-ND-AU S6-GR3P8K03-NV-ND-AU S6-GR3P9K03-NV-ND-AU S6-GR3P9.9K03-NV-ND-AU S6-GR3P10K03-NV-ND-AU Solis-25K-5G(-AU) Solis-30K-5G(-AU/-AU-MX/-BE) Solis-33K-5G(-AU) Solis-36K-5G(-AU) Solis-40K-5G(-AU) Solis-40K-HV-5G(-AU) Solis-50K-HV-5G(-AU) Solis-15K-LV-5G Solis-20K-LV-5G Solis-23K-LV-5G S5-GC25K(-AU) S5-GC30K(-AU/-BE) S5-GC33K(-AU) S5-GC36K(-AU) S5-GC40K(-AU) S5-GC40K-HV(-AU) S5-GC50K-HV(-AU) S5-GC15K-LV S5-GC20K-LV S5-GC23K-LV S5-GC37.5K S6-GC3P25K03-NV-ND S6-GC3P30K03-NV-ND S6-GC3P33K03-NV-ND S6-GC3P36K03-NV-ND S6-GC3P15K03-LV-ND S6-GC3P20K03-LV-ND S6-GC3P40K03-HV-ND S6-GC3P40K04-NV-ND S6-GC3P50K04-NV-ND S6-GC3P60K05-NV-ND S6-GC3P37.5K04-NV-ND S6-GC3P23K03-LV-ND S6-GC3P25K04-LV-ND S6-GC3P30K04-LV-ND S6-GC3P36K04-LV-ND S6-GC3P37.5K04-LV-ND S6-GC3P50K04-HV-ND S6-GC3P60K05-HV-ND S6-GC3P20K04-NV-ND-R S6-GC3P25K04-NV-ND-R S6-GC3P27.6K04-NV-ND-R S6-GC3P30K04-NV-ND-R S6-GC3P33K04-NV-ND-R S6-GC3P36K04-NV-ND-R S6-GC3P40K04-NV-ND-R S5-GC50K S5-GC60K S5-GC60K-HV S5-GC70K-HV S5-GC25K-LV S5-GC30K-LV S5-GC36K-LV S5-GC37.5K-LV Solis-50K-5G Solis-60K-5G Solis-60K-HV-5G Solis-70K-5G Solis-70K-HV-5G Solis-50K-LV-5G Solis-60K-LV-5G Solis-75K-5G(-US) Solis-80K-5G(-US) Solis-90K-5G(-US) Solis-100K-5G(-SA/-AU/-US) Solis-100K-HV-5G Solis-110K-5G(-SA/-AU) Solis-110K-BHV-5G Solis-125K-HV-5G(-AU) Solis-124K-HV-5G S5-GC50K-LV S5-GC60K-LV S5-GC125K-US S5-GC60K-LV-US S5-GC75K(-US) S5-GC80K(-US) S5-GC100K(-SA/-AU/-US) S5-GC110K(-SA/-AU) S5-GC100K-HV S5-GC124K-HV S5-GC125K-HV(-AU) S5-GC110K-BHV S5-GC90K(-US) Solis-50K-LV-5G-PRO Solis-60K-LV-5G-PRO Solis-75K-5G-PRO Solis-80K-5G-PRO Solis-100K-5G-PRO Solis-110K-5G-PRO Solis-120K-5G-PRO Solis-125K-5G-PRO Solis-75K-LV-5G-PRO Solis-125K-HV-5G-PRO S6-GC80K S6-GC100K S6-GC110K S6-GC125K S6-GC75K S6-GC50K-LV S6-GC60K-LV S6-GC75K-LV S6-GC125K-HV S6-GC3P100K10-HV-YD-US S6-GC3P124K10-HV-YD-US S6-GC3P125K10-HV-YD-US S6-GC3P150K10-HV-YD-US S6-GC3P60K08-LV-YD-US S6-GC3P75K08-LV-YD-US S6-GC3P80K07-LV-ND S6-GC3P100K07-LV-ND S6-GC3P150K07-NV-ND S6-GC3P200K07-HV-ND S6-GC3P150K07-HV-ND-US S6-GC3P166K07-HV-ND-US S6-GC3P174K07-HV-ND-US S6-GC3P200K07-HV-ND-US S7-GC3P150K07-NV-ND S7-GC3P200K07-HV-ND S7-GC3P80K07-LV-ND S7-GC3P100K07-LV-ND Solis-208K-EHV-5G Solis-215K-EHV-5G-PLUS Solis-250K-EHV-5G Solis-250K-EHV-5G-PLUS Solis-255K-EHV-5G Solis-255K-EHV-5G-PLUS Solis-125K-EHV-5G-PLUS Solis-185K-EHV-5G-US Solis-255K-EHV-5G-US Solis-185K-EHV-5G-US-PLUS Solis-255K-EHV-5G-US-PLUS Solis-125K-EHV-5G-US-PLUS Solis-100K-EHV-5G Solis-124K-EHV-5G Solis-125K-EHV-5G Solis-125K1-EHV-5G S6-GU300K-EHV-M12 S6-GU333K-EHV-M12 S6-GU350K-EHV-M12 S6-GU300K-EHV-M16 S6-GU333K-EHV-M16 S6-GU350K-EHV-M16 S6-GU250K-EHV-US-M12 S6-GU300K-EHV-US-M12 S6-GU350K-EHV-US-M12 S6-GU350K-EHV-US-M16 S6-GU3P275K06-EV-ND S6-GU3P300K06-EV-ND S6-GU3P333K06-EV-ND S6-GU3P350K06-EV-ND S6-GU3P200K02-DV-ND S6-GU3P250K02-CV-ND S6-GU3P350K02-EV-ND S6-GU3P250K06-CV-ND S6-GU3P200K02-DV-ND-US S6-GU3P250K02-CV-ND-US S6-GU3P350K02-EV-ND-US RHI-3P3K-HVES-5G RHI-3P4K-HVES-5G RHI-3P5K-HVES-5G RHI-3P6K-HVES-5G RHI-3P8K-HVES-5G RHI-3P10K-HVES-5G S6-EH3P3K-H-AU S6-EH3P4K-H-AU S6-EH3P5K-H-AU S6-EH3P6K-H-AU S6-EH3P8K-H-AU S6-EH3P10K-H-AU S6-EH3P3K-H-EU S6-EH3P4K-H-EU S6-EH3P5K-H-EU S6-EH3P6K-H-EU S6-EH3P8K-H-EU S6-EH3P10K-H-EU S6-EH3P8K-H-EU-PRO S6-EH3P10K-H-EU-PRO S6-EH3P5K2-H S6-EH3P6K2-H S6-EH3P8K2-H S6-EH3P10K2-H S6-EH3P3K-H-EU-OD S6-EH3P4K-H-EU-OD S6-EH3P5K-H-EU-OD S6-EH3P6K-H-EU-OD S6-EH3P8K-H-EU-OD S6-EH3P10K-H-EU-OD S6-EH3P10K-H-EU-PRO-OD S6-EH3P5K2-H-OD S6-EH3P6K2-H-OD S6-EH3P8K2-H-OD S6-EH3P10K2-H-OD S6-EH3P7K-H-LV S6-EA3P5KAA-NV-ND-H S6-EA3P6KAA-NV-ND-H S6-EA3P8KAA-NV-ND-H S6-EA3P10KAA-NV-ND-H S6-EH3P5K-H-EU(21A) S6-EH3P6K-H-EU(21A) S6-EH3P8K-H-EU(21A) S6-EH3P10K-H-EU(21A) S6-EH3P12K-H-EU(21A) S6-EH3P5K2-H(21A) S6-EH3P6K2-H(21A) S6-EH3P8K2-H(21A) S6-EH3P10K2-H(21A) S6-EH3P5K-H-AU(21A) S6-EH3P6K-H-AU(21A) S6-EH3P8K-H-AU(21A) S6-EH3P10K-H-AU(21A) S6-EH3P5K02-NV-YD-L S6-EH3P6K02-NV-YD-L S6-EH3P8K02-NV-YD-L S6-EH3P10K02-NV-YD-L S6-EH3P12K02-NV-YD-L S6-EH3P15K02-NV-YD-L S6-EH3P18K02-NV-YD-L S6-EH3P7K02-LV-YD-L S6-EH3P8K02-LV-YD-L S6-EH3P9K02-LV-YD-L S6-EH3P10K02-LV-YD-L S6-EH3P8K02-NV-YD-L-AU S6-EH3P9.9K02-NV-YD-L-AU S6-EH3P10K02-NV-YD-L-AU S6-EH3P12K02-NV-YD-L-AU S6-EH3P15K02-NV-YD-L-AU S7-EH3P5K03-NV-ND-D S7-EH3P6K03-NV-ND-D S7-EH3P8K03-NV-ND-D S7-EH3P10K04-NV-ND-D S7-EH3P12K04-NV-ND-D S7-EHP15K04-NV-ND-D S7-EHP20K04-NV-ND-D S7-EH3P5K03-NV-ND-D-AU S7-EH3P6K03-NV-ND-D-AU S7-EH3P8K04-NV-ND-D-AU S7-EH3P9.9K04-NV-ND-D-AU S7-EH3P10K04-NV-ND-D-AU S7-EH3P12K04-NV-ND-D-AU S7-EHP15K04-NV-ND-D-AU S7-EHP20K04-NV-ND-D-AU S6-EH2P5K02-SV-YD-L S6-EH2P6K02-SV-YD-L S6-EH2P7.5K02-SV-YD-L S6-EH2P7.5K02-SV-YD-L-PRO S6-EH2P8K02-SV-YD-L S6-EA3P5KAA-NV-YD-H-PRO S6-EA3P6KAA-NV-YD-H-PRO S6-EA3P8KAA-NV-YD-H-PRO S6-EA3P10KAA-NV-YD-H-PRO S6-EA3P5KAA-NV-ND-H-PRO S6-EA3P6KAA-NV-ND-H-PRO S6-EA3P8KAA-NV-ND-H-PRO S6-EA3P10KAA-NV-ND-H-PRO S6-EA3P7KAA-LV-ND-H-PRO S6-EH2P9.6K03-SV-YD-L-US S6-EH2P10K03-SV-YD-L-US S6-EH2P11.4K03-SV-YD-L-US S6-EH2P12K03-SV-YD-L-US S6-EH2P14K03-SV-YD-L-US S6-EH2P16K03-SV-YD-L-US S6-ER2P12K03-SV-YD-L-US-E S6-ER2P16K03-SV-YD-L-US-E S6-EH2P10K03-SV-YD-L S6-EH2P12K03-SV-YD-L S6-EH2P14K03-SV-YD-L S6-EH2P16K03-SV-YD-L S6-EH2P18K03-SV-YD-L S6-EH3P12K-H S6-EH3P15K-H S6-EH3P20K-H S6-EH3P12K-ND-H S6-EH3P15K-ND-H S6-EH3P20K-ND-H S6-EH3P8K-LV-H S6-EH3P10K-LV-H S6-EH3P12K-LV-H S6-EH3P8K-LV-ND-H S6-EH3P10K-LV-ND-H S6-EH3P12K-LV-ND-H S6-EH3P12K-H-AU S6-EH3P15K-H-AU S6-EH3P20K-H-AU S6-EH3P29.9K-H S6-EH3P30K-H S6-EH3P37.5K-H S6-EH3P40K-H S6-EH3P50K-H S6-EH3P30K-H-LV S6-EH3P29.9K-H-ND S6-EH3P30K-H-ND S6-EH3P40K-H-ND S6-EH3P49K-H-ND S6-EH3P50K-H-ND S6-EH3P30K-H-LV-ND S6-EH3P15K-H-LV-ND S6-EH3P20K-H-LV-ND S6-EH3P25K-H-LV-ND S6-EH3P29.9K-H(21A) S6-EH3P30K-H(21A) S6-EH3P37.5K-H(21A) S6-EH3P40K-H(21A) S6-EH3P49K-H(21A) S6-EH3P50K-H(21A) S6-EH3P60K-H(21A) S6-EH3P15K-H-LV(21A) S6-EH3P20K-H-LV(21A) S6-EH3P25K-H-LV(21A) S6-EH3P30K-H-LV(21A) S6-EH3P35K-H-LV(21A) S6-EH3P29.9K-H-ND(21A) S6-EH3P30K-H-ND(21A) S6-EH3P40K-H-ND(21A) S6-EH3P49K-H-ND(21A) S6-EH3P50K-H-ND(21A) S6-EH3P60K-H-ND(21A) S6-EH3P30K-H-LV-ND(21A) S6-EH3P15K-H-LV-ND(21A) S6-EH3P20K-H-LV-ND(21A) S6-EH3P25K-H-LV-ND(21A) S6-EH3P35K-H-LV-ND(21A) S6-EH3P29.9K-H-AU S6-EH3P30K-H-AU S6-EH3P40K-H-AU S6-EH3P50K-H-AU S6-EH3P30K-H-ND-AU S6-EH3P40K-H-ND-AU S6-EH3P50K-H-ND-AU S6-EH3P29.9K-H-AU(21A) S6-EH3P30K-H-AU(21A) S6-EH3P40K-H-AU(21A) S6-EH3P50K-H-AU(21A) S6-EH3P60K-H-AU(21A) S6-EH3P29.9K-H-ND-AU(21A) S6-EH3P30K-H-ND-AU(21A) S6-EH3P40K-H-ND-AU(21A) S6-EH3P50K-H-ND-AU(21A) S6-EH3P60K-H-ND-AU(21A) S6-EH3P30K03-NV-YD-H-US S6-EH3P40K04-NV-YD-H-US S6-EH3P50K04-NV-YD-H-US S6-EH3P60K04-NV-YD-H-US S6-EH3P30K03-LV-YD-H-US S6-EH3P30K03-LV-YD-H-US(21A) S6-EH3P30K03-NV-YD-H-US(21A) S6-EH3P40K04-NV-YD-H-US(21A) S6-EH3P50K04-NV-YD-H-US(21A) S6-EH3P60K04-NV-YD-H-US(21A) S6-EH3P75K10-NV-YD-H S6-EH3P80K10-NV-YD-H S6-EH3P99.9K10-NV-YD-H S6-EH3P100K10-NV-YD-H S6-EH3P125K10-NV-YD-H S6-EH3P80K10-NV-ND-H S6-EH3P99.9K10-NV-ND-H S6-EH3P100K10-NV-ND-H S6-EH3P125K10-NV-ND-H S6-EH3P60K10-LV-YD-H S6-EH3P75K10-LV-YD-H S6-EH3P60K10-LV-ND-H S6-EH3P75K10-LV-ND-H S6-EH3P80K10-NV-ND-H-AU S6-EH3P80K10-NV-YD-H-AU S6-EH3P100K10-NV-ND-H-AU S6-EH3P100K10-NV-YD-H-AU S6-EH3P125K10-NV-ND-H-AU S6-EH3P125K10-NV-YD-H-AU S6-EH3P60K10-LV-YD-H-US S6-EH3P75K10-LV-YD-H-US S6-EH3P100K10-NV-YD-H-US S6-EH3P125K10-NV-YD-H-US S6-EH3P150K10-NV-YD-H-US
Submitter Information
Full Name | Mr. Ruyi Pan
Job Title | Certification Manager
Company Name | Ginlong Technologies Co., Ltd.
Relationship to Manufacturer | Employee
Email | ruyi.pan@ginlong.com
Phone | 15888076344
Device Under Test Information
Test Type | SunSpec Modbus Conformance Certification
Firmware Version Tested | V04FD
Firmware Checksum (in hex) | 369a41f141875c896c202d250d52b733d66de2be5b879c04ac41bde66e5af7db(SHA256)
Interface Type | RTU
If RTU
Interface Name | COM12
Unit ID | 1
Baud Rate | 9600
Parity
Timeout (secs)
If Modbus TCP
IP Address
IP Port
Unit ID
If IEEE 2030.5
IP Address
IP Port
Poll Rate
Client PIN
Timeout (secs)
Reserved For SunSpec Alliance
SunSpec Certificate Number | SM-000056
Certificate Signer Name | Erin Mahan
Certificate Issued Date | 2026-06-16
Certificate Archive Location | https://sunspec.org/wp-content/uploads/2009/03/Ginlong_Modbus_Certificate_SM000056.pdf

## Test Lab Settings
Target Definition | Target Definition Label | Param | Param Label | Param Value

## IEEE 1547 Electrical Test Setup
Test Category | Param Definition | Param Definition Label | Param | Param Label | Param Unit | Param Value

## 1
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40002 | ID |  | 1 | R | 1 | 1
40003 | L |  | 66 | R
40004 | Mn |  | Ginlong | R
40020 | Md |  | S6-EH3 | R
40036 | Opt |  | 0553 | R
40044 | Vr |  | 04FD | R
40052 | SN |  | 1053290255300013 | R
40068 | DA |  | supported | RW | 1 | 247
40069 | Pad |  | 32768 | R

## 701
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40070 | ID |  | 701 | R | 701 | 701
40071 | L |  | 153 | R
40072 | ACType |  | supported | R
|  | SINGLE_PHASE | supported
|  | SPLIT_PHASE | supported
|  | THREE_PHASE | supported
40073 | St |  | supported | R
|  | OFF | supported
|  | ON | supported
40074 | InvSt |  | supported | R
|  | OFF | supported
|  | SLEEPING | supported
|  | STARTING | supported
|  | RUNNING | supported
|  | THROTTLED | supported
|  | SHUTTING_DOWN | supported
|  | FAULT | supported
|  | STANDBY | supported
40075 | ConnSt |  | supported | R
|  | DISCONNECTED | supported
|  | CONNECTED | supported
40076 | Alrm |  | supported | R
|  | GROUND_FAULT | supported
|  | DC_OVER_VOLT | supported
|  | AC_DISCONNECT | supported
|  | DC_DISCONNECT | supported
|  | GRID_DISCONNECT | supported
|  | CABINET_OPEN | supported
|  | MANUAL_SHUTDOWN | supported
|  | OVER_TEMP | supported
|  | OVER_FREQUENCY | supported
|  | UNDER_FREQUENCY | supported
|  | AC_OVER_VOLT | supported
|  | AC_UNDER_VOLT | supported
|  | BLOWN_STRING_FUSE | supported
|  | UNDER_TEMP | supported
|  | MEMORY_LOSS | supported
|  | HW_TEST_FAILURE | supported
|  | MANUFACTURER_ALRM | supported
40078 | DERMode |  | unimplemented | R
|  | GRID_FOLLOWING | unimplemented
|  | GRID_FORMING | unimplemented
|  | PV_CLIPPED | unimplemented
40080 | W |  | supported | R
40081 | VA |  | unimplemented | R
40082 | Var |  | supported | R
40083 | PF |  | supported | R
40084 | A |  | unimplemented | R
40085 | LLV |  | unimplemented | R
40086 | LNV |  | unimplemented | R
40087 | Hz |  | supported | R
40089 | TotWhInj |  | unimplemented | R
40093 | TotWhAbs |  | unimplemented | R
40097 | TotVarhInj |  | unimplemented | R
40101 | TotVarhAbs |  | unimplemented | R
40105 | TmpAmb |  | unimplemented | R
40106 | TmpCab |  | unimplemented | R
40107 | TmpSnk |  | unimplemented | R
40108 | TmpTrns |  | unimplemented | R
40109 | TmpSw |  | unimplemented | R
40110 | TmpOt |  | unimplemented | R
40111 | WL1 |  | unimplemented | R
40112 | VAL1 |  | unimplemented | R
40113 | VarL1 |  | unimplemented | R
40114 | PFL1 |  | unimplemented | R
40115 | AL1 |  | unimplemented | R
40116 | VL1L2 |  | unimplemented | R
40117 | VL1 |  | supported | R
40118 | TotWhInjL1 |  | unimplemented | R
40122 | TotWhAbsL1 |  | unimplemented | R
40126 | TotVarhInjL1 |  | unimplemented | R
40130 | TotVarhAbsL1 |  | unimplemented | R
40134 | WL2 |  | unimplemented | R
40135 | VAL2 |  | unimplemented | R
40136 | VarL2 |  | unimplemented | R
40137 | PFL2 |  | unimplemented | R
40138 | AL2 |  | unimplemented | R
40139 | VL2L3 |  | unimplemented | R
40140 | VL2 |  | supported | R
40141 | TotWhInjL2 |  | unimplemented | R
40145 | TotWhAbsL2 |  | unimplemented | R
40149 | TotVarhInjL2 |  | unimplemented | R
40153 | TotVarhAbsL2 |  | unimplemented | R
40157 | WL3 |  | unimplemented | R
40158 | VAL3 |  | unimplemented | R
40159 | VarL3 |  | unimplemented | R
40160 | PFL3 |  | unimplemented | R
40161 | AL3 |  | unimplemented | R
40162 | VL3L1 |  | unimplemented | R
40163 | VL3 |  | supported | R
40164 | TotWhInjL3 |  | unimplemented | R
40168 | TotWhAbsL3 |  | unimplemented | R
40172 | TotVarhInjL3 |  | unimplemented | R
40176 | TotVarhAbsL3 |  | unimplemented | R
40180 | ThrotPct |  | unimplemented | R
40181 | ThrotSrc |  | unimplemented | R
|  | MAX_W | unimplemented
|  | FIXED_W | unimplemented
|  | FIXED_VAR | unimplemented
|  | FIXED_PF | unimplemented
|  | VOLT_VAR | unimplemented
|  | FREQ_WATT | unimplemented
|  | DYN_REACT_CURR | unimplemented
|  | LVRT | unimplemented
|  | HVRT | unimplemented
|  | WATT_VAR | unimplemented
|  | VOLT_WATT | unimplemented
|  | SCHEDULED | unimplemented
|  | LFRT | unimplemented
|  | HFRT | unimplemented
|  | DERATED | unimplemented
40183 | A_SF |  | -1 | R
40184 | V_SF |  | -1 | R
40185 | Hz_SF |  | -2 | R
40186 | W_SF |  | 1 | R
40187 | PF_SF |  | -2 | R
40188 | VA_SF |  | -1 | R
40189 | Var_SF |  | -1 | R
40190 | TotWh_SF |  | 0 | R
40191 | TotVarh_SF |  | 0 | R
40192 | Tmp_SF |  | 0 | R
40193 | MnAlrmInfo |  | unimplemented | R

## 702
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40225 | ID |  | 702 | R | 702 | 702
40226 | L |  | 50 | R
40227 | WMaxRtg |  | 59464 | R
40228 | WOvrExtRtg |  | 34464 | R
40229 | WOvrExtRtgPF |  | 80 | R
40230 | WUndExtRtg |  | 34464 | R
40231 | WUndExtRtgPF |  | 80 | R
40232 | VAMaxRtg |  | 59464 | R
40233 | VarMaxInjRtg |  | 9464 | R
40234 | VarMaxAbsRtg |  | 9464 | R
40235 | WChaRteMaxRtg |  | 59464 | R
40236 | WDisChaRteMaxRtg |  | 59464 | R
40237 | VAChaRteMaxRtg |  | 59464 | R
40238 | VADisChaRteMaxRtg |  | 59464 | R
40239 | VNomRtg |  | 2300 | R
40240 | VMaxRtg |  | 2622 | R
40241 | VMinRtg |  | 2001 | R
40242 | AMaxRtg |  | unimplemented | R
40243 | PFOvrExtRtg |  | unimplemented | R
40244 | PFUndExtRtg |  | unimplemented | R
40245 | ReactSusceptRtg |  | 14200 | R
40246 | NorOpCatRtg |  | 1 | R
|  | CAT_A | supported
|  | CAT_B | supported
40247 | AbnOpCatRtg |  | 2 | R
|  | CAT_1 | supported
|  | CAT_2 | supported
|  | CAT_3 | supported
40248 | CtrlModes |  | 14335 | R
|  | MAX_W | supported
|  | FIXED_W | supported
|  | FIXED_VAR | supported
|  | FIXED_PF | supported
|  | VOLT_VAR | supported
|  | FREQ_WATT | supported
|  | DYN_REACT_CURR | supported
|  | LV_TRIP | supported
|  | HV_TRIP | supported
|  | WATT_VAR | supported
|  | VOLT_WATT | supported
|  | SCHEDULED | supported
|  | LF_TRIP | supported
|  | HF_TRIP | supported
40250 | IntIslandCatRtg |  | unimplemented | R
|  | UNCATEGORIZED | unimplemented
|  | INT_ISL_CAPABLE | unimplemented
|  | BLACK_START_CAPABLE | unimplemented
|  | ISOCH_CAPABLE | unimplemented
40251 | WMax |  | unimplemented | RW
40252 | WMaxOvrExt |  | unimplemented | RW
40253 | WOvrExtPF |  | unimplemented | RW
40254 | WMaxUndExt |  | unimplemented | RW
40255 | WUndExtPF |  | unimplemented | RW
40256 | VAMax |  | unimplemented | RW
40257 | VarMaxInj |  | unimplemented | RW
40258 | VarMaxAbs |  | unimplemented | RW
40259 | WChaRteMax |  | unimplemented | RW
40260 | WDisChaRteMax |  | unimplemented | RW
40261 | VAChaRteMax |  | unimplemented | RW
40262 | VADisChaRteMax |  | unimplemented | RW
40263 | VNom |  | unimplemented | RW
40264 | VMax |  | unimplemented | RW
40265 | VMin |  | unimplemented | RW
40266 | AMax |  | unimplemented | RW
40267 | PFOvrExt |  | unimplemented | RW
40268 | PFUndExt |  | unimplemented | RW
40269 | IntIslandCat |  | unimplemented | RW
|  | UNCATEGORIZED | unimplemented
|  | INT_ISL_CAPABLE | unimplemented
|  | BLACK_START_CAPABLE | unimplemented
|  | ISOCH_CAPABLE | unimplemented
40270 | W_SF |  | 0 | R
40271 | PF_SF |  | -2 | R
40272 | VA_SF |  | 0 | R
40273 | Var_SF |  | 0 | R
40274 | V_SF |  | -1 | R
40275 | A_SF |  | -1 | R
40276 | S_SF |  | -7 | R

## 703
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40277 | ID |  | 703 | R | 703 | 703
40278 | L |  | 17 | R
40279 | ES |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40280 | ESVHi |  | supported | RW | 100 | 130
40281 | ESVLo |  | supported | RW | 40 | 100
40282 | ESHzHi |  | supported | RW | 50 | 55
40284 | ESHzLo |  | supported | RW | 45 | 50
40286 | ESDlyTms |  | supported | RW | 0 | 1800
40288 | ESRndTms |  | supported | RW | 0 | 0
40290 | ESRmpTms |  | supported | RW | 2 | 6000
40292 | ESDlyRemTms |  | unimplemented | R
40294 | V_SF |  | -1 | R
40295 | Hz_SF |  | -2 | R

## 704
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40296 | ID |  | 704 | R | 704 | 704
40297 | L |  | 65 | R
40298 | PFWInjEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40299 | PFWInjEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40300 | PFWInjRvrtTms |  | unimplemented | RW
40302 | PFWInjRvrtRem |  | unimplemented | R
40304 | PFWAbsEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40305 | PFWAbsEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40306 | PFWAbsRvrtTms |  | unimplemented | RW
40308 | PFWAbsRvrtRem |  | unimplemented | R
40310 | WMaxLimPctEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40311 | WMaxLimPct |  | supported | RW | 0 | 100
40312 | WMaxLimPctRvrt |  | unimplemented | RW
40313 | WMaxLimPctEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40314 | WMaxLimPctRvrtTms |  | unimplemented | RW
40316 | WMaxLimPctRvrtRem |  | unimplemented | R
40318 | WSetEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40319 | WSetMod |  | supported | RW
|  | W_MAX_PCT | supported
|  | WATTS | supported
40320 | WSet |  | supported | RW | -125000 | 125000
40322 | WSetRvrt |  | unimplemented | RW
40324 | WSetPct |  | supported | RW | -100 | 100
40325 | WSetPctRvrt |  | unimplemented | RW
40326 | WSetEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40327 | WSetRvrtTms |  | unimplemented | RW
40329 | WSetRvrtRem |  | unimplemented | R
40331 | VarSetEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40332 | VarSetMod |  | supported | RW
|  | W_MAX_PCT | supported
|  | VAR_MAX_PCT | supported
|  | VAR_AVAIL_PCT | unimplemented
|  | VA_MAX_PCT | supported
|  | VARS | supported
40333 | VarSetPri |  | supported | RW
|  | ACTIVE | supported
|  | REACTIVE | supported
|  | VENDOR | unimplemented
40334 | VarSet |  | supported | RW | -75000 | 75000
40336 | VarSetRvrt |  | unimplemented | RW
40338 | VarSetPct |  | supported | RW | -60 | 60
40339 | VarSetPctRvrt |  | unimplemented | RW
40340 | VarSetEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40341 | VarSetRvrtTms |  | unimplemented | RW
40343 | VarSetRvrtRem |  | unimplemented | R
40345 | WRmp |  | unimplemented | RW
40346 | WRmpRef |  | unimplemented | RW
|  | A_MAX | unimplemented
|  | W_MAX | unimplemented
40347 | VarRmp |  | unimplemented | RW
40348 | AntiIslEna |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40349 | PF_SF |  | -3 | R
40350 | WMaxLimPct_SF |  | -2 | R
40351 | WSet_SF |  | -2 | R
40352 | WSetPct_SF |  | -2 | R
40353 | VarSet_SF |  | 0 | R
40354 | VarSetPct_SF |  | -2 | R
40355 | PFWInj.PF |  | supported | RW | 0.8 | 1
40356 | PFWInj.Ext |  | supported | RW
|  | OVER_EXCITED | supported
|  | UNDER_EXCITED | supported
40357 | PFWInjRvrt.PF |  | unimplemented | RW
40358 | PFWInjRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented
40359 | PFWAbs.PF |  | supported | RW | 0.85 | 1
40360 | PFWAbs.Ext |  | supported | RW
|  | OVER_EXCITED | supported
|  | UNDER_EXCITED | supported
40361 | PFWAbsRvrt.PF |  | unimplemented | RW
40362 | PFWAbsRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented