## Product and Testing Info
Product Information
Product Type | Inverter
Manufacturer Name | MUST ENERGY (GUANGDONG) TECHNOLOGY CO.,LTD
Product Name | ENERGY STORAGE INVERTER
Product Model Numbers | PH11-5KL3-EU PH11-6.5KL3-EU PH11-8KL3-EU PH11-10KL3-EU PH11-12KL3-EU PH11-5KW EU PH11-6.5KW EU PH11-8KW EU PH11-10KW EU PH11-12KW EU PH11-5KL3 EU PH11-6.5KL3 EU PH11-8KL3 EU PH11-10KL3 EU PH11-12KL3 EU PH11-5048 PRO PH11-6548 PRO PH11-8048 PRO PH11-10048 PRO PH11-12048 PRO PH1100-5KL3-EU PH1100-6.5KL3-EU PH1100-8KL3-EU PH1100-10KL3-EU PH1100-12KL3-EU PH1100-5KLS EU PH1100-6.5KLS EU PH1100-8KLS EU PH1100-10KLS EU PH1100-12KLS EU BHF11 EXP10048 EU KL3 PH11-12048PRO PH11-5048 L3-EU PH11-6548 L3-EU PH11-8048 L3-EU PH11-10048 L3-EU PH11-12048 L3-EU PH11-10048 PRO L3-EU PH11-12048 PRO L3-EU PH11-13KL3-EU PH11-14KL3-EU PH11-15KL3-EU PH11-16KL3-EU PH11-17KL3-EU PH11-18KL3-EU PH11-19KL3-EU PH11-20KL3-EU PH11-5KL3-EU-HV PH11-6KL3-EU-HV PH11-8KL3-EU-HV PH11-10KL3-EU-HV PH11-12KL3-EU-HV PH11-15KL3-EU-HV PH11-20KL3-EU-HV PH11-25KL3-EU-HV PH11-30KL3-EU-HV PH11-50KL3-EU-HV PH11-3048PRO PH11-3648PRO PH11-4048PRO PH11-4648PRO PH11-5048PRO PH11-6048PRO PH11-7048PRO PH11-7248PRO PH11-8048PRO PH11-8248PRO PH11-9048PRO PH11-9248PRO PH11-10048PRO PH11-10248PRO PH11-3.6KW Pro PH11-4KW Pro PH11-4.6KW Pro PH11-5KW Pro PH11-6KW Pro PH11-6KW PRO PH1100-3648 PRO PH1100-4048 PRO PH1100-4648 PRO PH1100-5048 PRO PH1100-6048 PRO PH11-3KL1-EU-G2 PH11-3.6KL1-EU-G2 PH11-4KL1-EU-G2 PH11-4.6KL1-EU-G2 PH11-5KL1-EU-G2 PH11-6KL1-EU-G2 PH11-7KL1-EU-G2 PH11-7.6KL1-EU-G2 PH11-8KL1-EU-G2 PH11-5KL2-US-G2 PH11-6KL2-US-G2 PH11-7.6KL2-US-G2 PH11-8KL2-US-G2 PH11-10KL2-US-G2 PH11-12KL2-US-G2 PH11-5KL1-EU PH11-6KL1-EU PH11-8KL1-EU PH11-10KL1-EU PH11-5KL2-US PH11-6KL2-US PH11-8KL2-US PH11-10KL2-US PH11-11KL2-US PH11-12KL2-US
Submitter Information
Full Name | Peng Chen
Job Title | Test supervisor
Company Name | MUST ENERGY (GUANGDONG) TECHNOLOGY CO.,LTD
Relationship to Manufacturer | Employee
Email | rd-cp@mustpower.cn
Phone | +86 15012636534
Device Under Test Information
Test Type | SunSpec Modbus Conformance Certification
Firmware Version Tested | V00.01
Firmware Checksum (in hex) | fb484c932aa3af3c3a29caece39e8636
Interface Type | RTU
If RTU
Interface Name | COM6
Unit ID | 4
Baud Rate | 19200
Parity | None
Timeout (secs) | 15
If Modbus TCP
IP Address
IP Port
Unit ID
If IEEE 2030.5
IP Address
IP Port
Poll Rate
Client PIN
Timeout (secs)
SunSpec Certificate Number | SM-000044
Certificate Signer Name | Dylan Tansy
Certificate Issued Date | 2025-06-13
Certificate Archive Location | https://sunspec.org/wp-content/uploads/2009/03/Must-Energy_Modbus-Certificate_SM000044.pdf

## Test Lab Settings
Target Definition | Target Definition Label | Param | Param Label | Param Value

## IEEE 1547 Electrical Test Setup
Test Category | Param Definition | Param Definition Label | Param | Param Label | Param Unit | Param Value

## 1
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40002 | ID |  | 1 | R | 1 | 1
40003 | L |  | 66 | R
40004 | Mn |  | MUST | R
40020 | Md |  | Energy Storage Inverter | R
40036 | Opt |  | PH11 | R
40044 | Vr |  | 00.01 | R
40052 | SN |  | 064042504300157 | R
40068 | DA |  | supported | RW | 0 | 247
40069 | Pad |  | 65535 | R

## 701
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40070 | ID |  | 701 | R | 701 | 701
40071 | L |  | 153 | R
40072 | ACType |  | supported | R
|  | SINGLE_PHASE | supported
|  | SPLIT_PHASE | supported
|  | THREE_PHASE | supported
40073 | St |  | supported | R
|  | OFF | supported
|  | ON | supported
40074 | InvSt |  | supported | R
|  | OFF | supported
|  | SLEEPING | supported
|  | STARTING | supported
|  | RUNNING | supported
|  | THROTTLED | supported
|  | SHUTTING_DOWN | supported
|  | FAULT | supported
|  | STANDBY | supported
40075 | ConnSt |  | supported | R
|  | DISCONNECTED | supported
|  | CONNECTED | supported
40076 | Alrm |  | supported | R
|  | GROUND_FAULT | supported
|  | DC_OVER_VOLT | supported
|  | AC_DISCONNECT | supported
|  | DC_DISCONNECT | supported
|  | GRID_DISCONNECT | supported
|  | CABINET_OPEN | supported
|  | MANUAL_SHUTDOWN | supported
|  | OVER_TEMP | supported
|  | OVER_FREQUENCY | supported
|  | UNDER_FREQUENCY | supported
|  | AC_OVER_VOLT | supported
|  | AC_UNDER_VOLT | supported
|  | BLOWN_STRING_FUSE | supported
|  | UNDER_TEMP | supported
|  | MEMORY_LOSS | supported
|  | HW_TEST_FAILURE | supported
|  | MANUFACTURER_ALRM | supported
40078 | DERMode |  | supported | R
|  | GRID_FOLLOWING | supported
|  | GRID_FORMING | supported
|  | PV_CLIPPED | supported
40080 | W |  | supported | R
40081 | VA |  | supported | R
40082 | Var |  | supported | R
40083 | PF |  | supported | R
40084 | A |  | supported | R
40085 | LLV |  | unimplemented | R
40086 | LNV |  | supported | R
40087 | Hz |  | supported | R
40089 | TotWhInj |  | supported | R
40093 | TotWhAbs |  | supported | R
40097 | TotVarhInj |  | unimplemented | R
40101 | TotVarhAbs |  | unimplemented | R
40105 | TmpAmb |  | supported | R
40106 | TmpCab |  | supported | R
40107 | TmpSnk |  | supported | R
40108 | TmpTrns |  | supported | R
40109 | TmpSw |  | supported | R
40110 | TmpOt |  | supported | R
40111 | WL1 |  | supported | R
40112 | VAL1 |  | supported | R
40113 | VarL1 |  | supported | R
40114 | PFL1 |  | supported | R
40115 | AL1 |  | supported | R
40116 | VL1L2 |  | unimplemented | R
40117 | VL1 |  | supported | R
40118 | TotWhInjL1 |  | unimplemented | R
40122 | TotWhAbsL1 |  | unimplemented | R
40126 | TotVarhInjL1 |  | unimplemented | R
40130 | TotVarhAbsL1 |  | unimplemented | R
40134 | WL2 |  | supported | R
40135 | VAL2 |  | supported | R
40136 | VarL2 |  | supported | R
40137 | PFL2 |  | supported | R
40138 | AL2 |  | supported | R
40139 | VL2L3 |  | unimplemented | R
40140 | VL2 |  | supported | R
40141 | TotWhInjL2 |  | unimplemented | R
40145 | TotWhAbsL2 |  | unimplemented | R
40149 | TotVarhInjL2 |  | unimplemented | R
40153 | TotVarhAbsL2 |  | unimplemented | R
40157 | WL3 |  | supported | R
40158 | VAL3 |  | supported | R
40159 | VarL3 |  | supported | R
40160 | PFL3 |  | supported | R
40161 | AL3 |  | supported | R
40162 | VL3L1 |  | unimplemented | R
40163 | VL3 |  | supported | R
40164 | TotWhInjL3 |  | unimplemented | R
40168 | TotWhAbsL3 |  | unimplemented | R
40172 | TotVarhInjL3 |  | unimplemented | R
40176 | TotVarhAbsL3 |  | unimplemented | R
40180 | ThrotPct |  | supported | R
40181 | ThrotSrc |  | unimplemented | R
|  | MAX_W | unimplemented
|  | FIXED_W | unimplemented
|  | FIXED_VAR | unimplemented
|  | FIXED_PF | unimplemented
|  | VOLT_VAR | unimplemented
|  | FREQ_WATT | unimplemented
|  | DYN_REACT_CURR | unimplemented
|  | LVRT | unimplemented
|  | HVRT | unimplemented
|  | WATT_VAR | unimplemented
|  | VOLT_WATT | unimplemented
|  | SCHEDULED | unimplemented
|  | LFRT | unimplemented
|  | HFRT | unimplemented
|  | DERATED | unimplemented
40183 | A_SF |  | -1 | R
40184 | V_SF |  | -1 | R
40185 | Hz_SF |  | -2 | R
40186 | W_SF |  | 0 | R
40187 | PF_SF |  | -1 | R
40188 | VA_SF |  | -1 | R
40189 | Var_SF |  | -1 | R
40190 | TotWh_SF |  | -1 | R
40191 | TotVarh_SF |  | 0 | R
40192 | Tmp_SF |  | -1 | R
40193 | MnAlrmInfo |  | supported | R

## 702
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40225 | ID |  | 702 | R | 702 | 702
40226 | L |  | 50 | R
40227 | WMaxRtg |  | 12000 | R
40228 | WOvrExtRtg |  | 12000 | R
40229 | WOvrExtRtgPF |  | 8 | R
40230 | WUndExtRtg |  | 12000 | R
40231 | WUndExtRtgPF |  | 8 | R
40232 | VAMaxRtg |  | 13200 | R
40233 | VarMaxInjRtg |  | 9000 | R
40234 | VarMaxAbsRtg |  | 0 | R
40235 | WChaRteMaxRtg |  | 12000 | R
40236 | WDisChaRteMaxRtg |  | 12000 | R
40237 | VAChaRteMaxRtg |  | 12000 | R
40238 | VADisChaRteMaxRtg |  | 13200 | R
40239 | VNomRtg |  | 400 | R
40240 | VMaxRtg |  | 460 | R
40241 | VMinRtg |  | 340 | R
40242 | AMaxRtg |  | 5220 | R
40243 | PFOvrExtRtg |  | 8 | R
40244 | PFUndExtRtg |  | 8 | R
40245 | ReactSusceptRtg |  | 12000 | R
40246 | NorOpCatRtg |  | 1 | R
|  | CAT_A | supported
|  | CAT_B | supported
40247 | AbnOpCatRtg |  | 2 | R
|  | CAT_1 | supported
|  | CAT_2 | supported
|  | CAT_3 | supported
40248 | CtrlModes |  | unimplemented | R
|  | MAX_W | unimplemented
|  | FIXED_W | unimplemented
|  | FIXED_VAR | unimplemented
|  | FIXED_PF | unimplemented
|  | VOLT_VAR | unimplemented
|  | FREQ_WATT | unimplemented
|  | DYN_REACT_CURR | unimplemented
|  | LV_TRIP | unimplemented
|  | HV_TRIP | unimplemented
|  | WATT_VAR | unimplemented
|  | VOLT_WATT | unimplemented
|  | SCHEDULED | unimplemented
|  | LF_TRIP | unimplemented
|  | HF_TRIP | unimplemented
40250 | IntIslandCatRtg |  | unimplemented | R
|  | UNCATEGORIZED | unimplemented
|  | INT_ISL_CAPABLE | unimplemented
|  | BLACK_START_CAPABLE | unimplemented
|  | ISOCH_CAPABLE | unimplemented
40251 | WMax |  | supported | RW | 0 | 12000
40252 | WMaxOvrExt |  | unimplemented | RW
40253 | WOvrExtPF |  | unimplemented | RW
40254 | WMaxUndExt |  | unimplemented | RW
40255 | WUndExtPF |  | unimplemented | RW
40256 | VAMax |  | unimplemented | RW
40257 | VarMaxInj |  | unimplemented | RW
40258 | VarMaxAbs |  | unimplemented | RW
40259 | WChaRteMax |  | unimplemented | RW
40260 | WDisChaRteMax |  | unimplemented | RW
40261 | VAChaRteMax |  | unimplemented | RW
40262 | VADisChaRteMax |  | unimplemented | RW
40263 | VNom |  | unimplemented | RW
40264 | VMax |  | unimplemented | RW
40265 | VMin |  | unimplemented | RW
40266 | AMax |  | unimplemented | RW
40267 | PFOvrExt |  | unimplemented | RW
40268 | PFUndExt |  | unimplemented | RW
40269 | IntIslandCat |  | supported | RW
|  | UNCATEGORIZED | supported
|  | INT_ISL_CAPABLE | supported
|  | BLACK_START_CAPABLE | supported
|  | ISOCH_CAPABLE | supported
40270 | W_SF |  | 0 | R
40271 | PF_SF |  | -1 | R
40272 | VA_SF |  | 0 | R
40273 | Var_SF |  | 0 | R
40274 | V_SF |  | 0 | R
40275 | A_SF |  | -2 | R
40276 | S_SF |  | 0 | R

## 714
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40277 | ID |  | 714 | R | 714 | 714
40278 | L |  | 68 | R
40279 | PrtAlrms |  | unimplemented | R
40281 | NPrt |  | 2 | R
40282 | DCA |  | supported | R
40283 | DCW |  | supported | R
40284 | DCWhInj |  | supported | R
40288 | DCWhAbs |  | supported | R
40292 | DCA_SF |  | -1 | R
40293 | DCV_SF |  | -1 | R
40294 | DCW_SF |  | 0 | R
40295 | DCWH_SF |  | -1 | R
40296 | Tmp_SF |  | -1 | R
40297 | Prt.1.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
40298 | Prt.1.ID |  | supported | R
40299 | Prt.1.IDStr |  | supported | R
40307 | Prt.1.DCA |  | supported | R
40308 | Prt.1.DCV |  | supported | R
40309 | Prt.1.DCW |  | supported | R
40310 | Prt.1.DCWhInj |  | unimplemented | R
40314 | Prt.1.DCWhAbs |  | unimplemented | R
40318 | Prt.1.Tmp |  | supported | R
40319 | Prt.1.DCSta |  | unimplemented | R
|  | OFF | unimplemented
|  | ON | unimplemented
|  | WARNING | unimplemented
|  | ERROR | unimplemented
40320 | Prt.1.DCAlrm |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | INPUT_OVER_VOLTAGE | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | BLOWN_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | ARC_DETECTION | unimplemented
|  | RESERVED | unimplemented
|  | TEST_FAILED | unimplemented
|  | INPUT_UNDER_VOLTAGE | unimplemented
|  | INPUT_OVER_CURRENT | unimplemented
40322 | Prt.2.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
40323 | Prt.2.ID |  | supported | R
40324 | Prt.2.IDStr |  | supported | R
40332 | Prt.2.DCA |  | supported | R
40333 | Prt.2.DCV |  | supported | R
40334 | Prt.2.DCW |  | supported | R
40335 | Prt.2.DCWhInj |  | unimplemented | R
40339 | Prt.2.DCWhAbs |  | unimplemented | R
40343 | Prt.2.Tmp |  | supported | R
40344 | Prt.2.DCSta |  | unimplemented | R
|  | OFF | unimplemented
|  | ON | unimplemented
|  | WARNING | unimplemented
|  | ERROR | unimplemented
40345 | Prt.2.DCAlrm |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | INPUT_OVER_VOLTAGE | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | BLOWN_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | ARC_DETECTION | unimplemented
|  | RESERVED | unimplemented
|  | TEST_FAILED | unimplemented
|  | INPUT_UNDER_VOLTAGE | unimplemented
|  | INPUT_OVER_CURRENT | unimplemented