## Instructions
DER Security Corp
IEEE-1547 Protocol Information Conformance Statement (PICS)
For manufacturers of DER devices that must comply with IEEE 1547-2018 and UL 1741 SB.
This file was generated by SunSpec Dashboard or DER Security LabTest software. It is used to prepare and submit a product for testing at a Nationally Recognized Testing Lab (for electrical function validation and certification) or a SunSpec Authorized Testing laboratory (for SunSpec Modbus and/or IEEE 2030.5 communication protocol validation and certification). Some data is input by the user into the SunSpec Dashboard or DER Security LabTest software prior to autogenerating this spreadsheet and some data is read from Equipment Under Test (EUT) by SunSpec Dashboard or DER Security LabTest software after the spreadsheet is generated.
The Product and Testing Info tab contains general information about the unit under test, the manufacturer of the product, and the test laboratory network setup. It also contains an area for test laboratory personnel to enter information about an IEEE 1547 test that has previously been run on the unit under test.
The Test Lab Settings tab contains information about the testing laboratory and test engineer that ran a test. Data is input to this tab by the test engineer after a test run is completed.
The IEEE 1547 Electrical Test Setup tab contains information needed to configure the EUT for electrical testing according the IEEE 1547.1 standard. Most parameters are defined in the IEEE 1547.1 "Test Requirements" section (section 5.14.2) and some were by DER Security Corp to facilitate electrical test setup.
Numerical Tab names refer to the specific SunSpec Modbus models contained in the EUT and tab names that start with "2030.5 CSIP-" refer to specific IEEE 2030.5 capabilities of the product that the EUT will be evaluated against.
DER Security Corp License Agreement and Copyright
This document and the information contained herein is provided on an "AS IS" basis and the DER Security Corp DISCLAIMS ALL WARRANTIES, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY WARRANTY THAT THE USE OF THE INFORMATION HEREIN WILL NOT INFRINGE ANY OWNERSHIP RIGHTS OR ANY IMPLIED WARRANTIES OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE.
This document may be used, copied, and furnished to others, without restrictions of any kind, provided that this document itself may not be modified in anyway, except as needed by the DER Security Corp Technical Committee and as governed by the DER Security Corp IPR Policy. The complete policy of DER Security Corp can be found at https://www.dersec.io/.

## Product and Testing Info
Product Information
Product Type | Inverter
Manufacturer Name | Guangzhou Felicity Solar Technology Co.,Ltd.
Product Name | Hybrid Inverter
Product Model Numbers | IVGM125KHP3G1,IVGM100KHP3G1,IVGM80KHP3G1,IVGM75KHP3G1;IVGM50KHP3G2,IVGM40KHP3G2,IVGM30KHP3G2,IVGM29K9HP3G2,IVGM25KHP3G2;IVGM20KLP3G1,IVGM18KLP3G1,IVGM16KLP3G1,IVGM15KLP3G1,IVGM14KLP3G1,IVGM12KLP3G1,IVGM10KLP3G1;IVGM12KLP3G2,IVGM10KLP3G2,IVGM8KLP3G2,IVGM6KLP3G2,IVGM5KLP3G2,IVGM4KLP3G2,IVGM3KLP3G2;IVGM8KLP1G1,IVGM7K6LP1G1,IVGM6KLP1G1,IVGM5KLP1G1;IVGM6KLP1G2,IVGM5KLP1G2,IVGM3K6LP1G2,IVGM3KLP1G2,IVGM3KLP1G2-24;IVGM16KLP1G1,IVGM14KLP1G1,IVGM12KLP1G1；IVGM25KHP3G3, IVGM20KHP3G3, IVGM15KHP3G3, IVGM12KHP3G3,IVGM10KHP3G3, IVGM9K9HP3G3, IVGM8KHP3G3.
Submitter Information
Full Name | Simin Deng
Job Title | Certification Engineer
Company Name | Guangzhou Felicity Solar Technology Co.,Ltd.
Relationship to Manufacturer | Employee
Email | dengsimin@felicitysolar.com
Phone | +86 13242889373
Device Under Test Information
Test Type | SunSpec Modbus Conformance Certification
Firmware Version Tested | 100
Firmware Checksum (in hex) | 0x039CF00A
Interface Type | Modbus TCP
If RTU
Interface Name | COM3
Unit ID | 1
Baud Rate | 9600
Parity | None
Timeout (secs) | 15
If Modbus TCP
IP Address | 183.6.68.229
IP Port | 8099
Unit ID | 1
If IEEE 2030.5
IP Address
IP Port
Poll Rate
Client PIN
Timeout (secs)
Reserved For SunSpec Alliance
SunSpec Certificate Number | SM-000061
Certificate Signer Name | Erin Mahan
Certificate Issued Date | 2026-09-15
Certificate Archive Location | https://sunspec.org/wp-content/uploads/2009/03/FINAL_Felicity_Modbus_Certificate_SM000061.pdf

## Test Lab Settings
Target Definition | Target Definition Label | Param | Param Label | Param Value

## IEEE 1547 Electrical Test Setup
Test Category | Param Definition | Param Definition Label | Param | Param Label | Param Unit | Param Value

## 1
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50002 | ID |  | 1 | R | 1 | 1
50003 | L |  | 66 | R
50004 | Mn |  | Felicity Solar Technology | R
50020 | Md |  | IVGM50KHP3G2 | R
50036 | Opt |  | unimplemented | R
50044 | Vr |  | 100 | R
50052 | SN |  | 130500060026230005 | R
50068 | DA |  | supported | RW | 0 | 247
50069 | Pad |  | 0 | R

## 701
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50070 | ID |  | 701 | R | 701 | 701
50071 | L |  | 153 | R
50072 | ACType |  | supported | R
|  | SINGLE_PHASE | supported
|  | SPLIT_PHASE | supported
|  | THREE_PHASE | supported
50073 | St |  | supported | R
|  | OFF | supported
|  | ON | supported
50074 | InvSt |  | supported | R
|  | OFF | supported
|  | SLEEPING | supported
|  | STARTING | supported
|  | RUNNING | supported
|  | THROTTLED | supported
|  | SHUTTING_DOWN | supported
|  | FAULT | supported
|  | STANDBY | supported
50075 | ConnSt |  | supported | R
|  | DISCONNECTED | supported
|  | CONNECTED | supported
50076 | Alrm |  | supported | R
|  | GROUND_FAULT | supported
|  | DC_OVER_VOLT | supported
|  | AC_DISCONNECT | supported
|  | DC_DISCONNECT | supported
|  | GRID_DISCONNECT | supported
|  | CABINET_OPEN | supported
|  | MANUAL_SHUTDOWN | supported
|  | OVER_TEMP | supported
|  | OVER_FREQUENCY | supported
|  | UNDER_FREQUENCY | supported
|  | AC_OVER_VOLT | supported
|  | AC_UNDER_VOLT | supported
|  | BLOWN_STRING_FUSE | supported
|  | UNDER_TEMP | supported
|  | MEMORY_LOSS | supported
|  | HW_TEST_FAILURE | supported
|  | MANUFACTURER_ALRM | supported
50078 | DERMode |  | supported | R
|  | GRID_FOLLOWING | supported
|  | GRID_FORMING | supported
|  | PV_CLIPPED | supported
50080 | W |  | supported | R
50081 | VA |  | supported | R
50082 | Var |  | supported | R
50083 | PF |  | supported | R
50084 | A |  | supported | R
50085 | LLV |  | supported | R
50086 | LNV |  | supported | R
50087 | Hz |  | supported | R
50089 | TotWhInj |  | supported | R
50093 | TotWhAbs |  | supported | R
50097 | TotVarhInj |  | supported | R
50101 | TotVarhAbs |  | supported | R
50105 | TmpAmb |  | supported | R
50106 | TmpCab |  | supported | R
50107 | TmpSnk |  | supported | R
50108 | TmpTrns |  | supported | R
50109 | TmpSw |  | supported | R
50110 | TmpOt |  | supported | R
50111 | WL1 |  | supported | R
50112 | VAL1 |  | supported | R
50113 | VarL1 |  | supported | R
50114 | PFL1 |  | supported | R
50115 | AL1 |  | supported | R
50116 | VL1L2 |  | supported | R
50117 | VL1 |  | supported | R
50118 | TotWhInjL1 |  | supported | R
50122 | TotWhAbsL1 |  | supported | R
50126 | TotVarhInjL1 |  | supported | R
50130 | TotVarhAbsL1 |  | supported | R
50134 | WL2 |  | supported | R
50135 | VAL2 |  | supported | R
50136 | VarL2 |  | supported | R
50137 | PFL2 |  | supported | R
50138 | AL2 |  | supported | R
50139 | VL2L3 |  | supported | R
50140 | VL2 |  | supported | R
50141 | TotWhInjL2 |  | supported | R
50145 | TotWhAbsL2 |  | supported | R
50149 | TotVarhInjL2 |  | supported | R
50153 | TotVarhAbsL2 |  | supported | R
50157 | WL3 |  | supported | R
50158 | VAL3 |  | supported | R
50159 | VarL3 |  | supported | R
50160 | PFL3 |  | supported | R
50161 | AL3 |  | supported | R
50162 | VL3L1 |  | supported | R
50163 | VL3 |  | supported | R
50164 | TotWhInjL3 |  | supported | R
50168 | TotWhAbsL3 |  | supported | R
50172 | TotVarhInjL3 |  | supported | R
50176 | TotVarhAbsL3 |  | supported | R
50180 | ThrotPct |  | supported | R
50181 | ThrotSrc |  | supported | R
|  | MAX_W | supported
|  | FIXED_W | supported
|  | FIXED_VAR | supported
|  | FIXED_PF | supported
|  | VOLT_VAR | supported
|  | FREQ_WATT | supported
|  | DYN_REACT_CURR | supported
|  | LVRT | supported
|  | HVRT | supported
|  | WATT_VAR | supported
|  | VOLT_WATT | supported
|  | SCHEDULED | supported
|  | LFRT | supported
|  | HFRT | supported
|  | DERATED | supported
50183 | A_SF |  | -1 | R
50184 | V_SF |  | -1 | R
50185 | Hz_SF |  | -2 | R
50186 | W_SF |  | 1 | R
50187 | PF_SF |  | -2 | R
50188 | VA_SF |  | 1 | R
50189 | Var_SF |  | 1 | R
50190 | TotWh_SF |  | 2 | R
50191 | TotVarh_SF |  | 2 | R
50192 | Tmp_SF |  | 0 | R
50193 | MnAlrmInfo |  | unimplemented | R

## 702
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50225 | ID |  | 702 | R | 702 | 702
50226 | L |  | 50 | R
50227 | WMaxRtg |  | 50000 | R
50228 | WOvrExtRtg |  | 45000 | R
50229 | WOvrExtRtgPF |  | 90 | R
50230 | WUndExtRtg |  | 45000 | R
50231 | WUndExtRtgPF |  | 90 | R
50232 | VAMaxRtg |  | 50000 | R
50233 | VarMaxInjRtg |  | 21794 | R
50234 | VarMaxAbsRtg |  | 21794 | R
50235 | WChaRteMaxRtg |  | 50000 | R
50236 | WDisChaRteMaxRtg |  | 50000 | R
50237 | VAChaRteMaxRtg |  | 50000 | R
50238 | VADisChaRteMaxRtg |  | 50000 | R
50239 | VNomRtg |  | 4800 | R
50240 | VMaxRtg |  | 5520 | R
50241 | VMinRtg |  | 3840 | R
50242 | AMaxRtg |  | 602 | R
50243 | PFOvrExtRtg |  | 0 | R
50244 | PFUndExtRtg |  | 0 | R
50245 | ReactSusceptRtg |  | 0 | R
50246 | NorOpCatRtg |  | 1 | R
|  | CAT_A | supported
|  | CAT_B | supported
50247 | AbnOpCatRtg |  | 2 | R
|  | CAT_1 | supported
|  | CAT_2 | supported
|  | CAT_3 | supported
50248 | CtrlModes |  | 14271 | R
|  | MAX_W | supported
|  | FIXED_W | supported
|  | FIXED_VAR | supported
|  | FIXED_PF | supported
|  | VOLT_VAR | supported
|  | FREQ_WATT | supported
|  | DYN_REACT_CURR | supported
|  | LV_TRIP | supported
|  | HV_TRIP | supported
|  | WATT_VAR | supported
|  | VOLT_WATT | supported
|  | SCHEDULED | supported
|  | LF_TRIP | supported
|  | HF_TRIP | supported
50250 | IntIslandCatRtg |  | 0 | R
|  | UNCATEGORIZED | supported
|  | INT_ISL_CAPABLE | supported
|  | BLACK_START_CAPABLE | supported
|  | ISOCH_CAPABLE | supported
50251 | WMax |  | supported | RW | 0 | 50000
50252 | WMaxOvrExt |  | supported | RW | 0 | 50000
50253 | WOvrExtPF |  | supported | RW | 0.9 | 1
50254 | WMaxUndExt |  | supported | RW | 0 | 50000
50255 | WUndExtPF |  | supported | RW | 0.9 | 1
50256 | VAMax |  | supported | RW | 0 | 50000
50257 | VarMaxInj |  | supported | RW | 0 | 21794
50258 | VarMaxAbs |  | supported | RW | 0 | 21794
50259 | WChaRteMax |  | supported | RW | 0 | 0
50260 | WDisChaRteMax |  | supported | RW | 0 | 0
50261 | VAChaRteMax |  | supported | RW | 0 | 0
50262 | VADisChaRteMax |  | supported | RW | 0 | 0
50263 | VNom |  | supported | RW | 384 | 552
50264 | VMax |  | supported | RW | 384 | 552
50265 | VMin |  | supported | RW | 384 | 552
50266 | AMax |  | supported | RW | 0 | 60.2
50267 | PFOvrExt |  | supported | RW | 0 | 1
50268 | PFUndExt |  | supported | RW | 0 | 1
50269 | IntIslandCat |  | supported | RW | 0 | 0
|  | UNCATEGORIZED | supported
|  | INT_ISL_CAPABLE | supported
|  | BLACK_START_CAPABLE | supported
|  | ISOCH_CAPABLE | supported
50270 | W_SF |  | 0 | R
50271 | PF_SF |  | -2 | R
50272 | VA_SF |  | 0 | R
50273 | Var_SF |  | 0 | R
50274 | V_SF |  | -1 | R
50275 | A_SF |  | -1 | R
50276 | S_SF |  | 0 | R

## 703
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50277 | ID |  | 703 | R | 703 | 703
50278 | L |  | 17 | R
50279 | ES |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50280 | ESVHi |  | supported | RW | 105 | 106
50281 | ESVLo |  | supported | RW | 88 | 95
50282 | ESHzHi |  | supported | RW | 60.1 | 61
50284 | ESHzLo |  | supported | RW | 59 | 59.9
50286 | ESDlyTms |  | supported | RW | 0 | 600
50288 | ESRndTms |  | supported | RW | 0 | 1000
50290 | ESRmpTms |  | supported | RW | 1 | 1000
50292 | ESDlyRemTms |  | supported | R
50294 | V_SF |  | 0 | R
50295 | Hz_SF |  | -2 | R

## 704
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50296 | ID |  | 704 | R | 704 | 704
50297 | L |  | 65 | R
50298 | PFWInjEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50299 | PFWInjEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50300 | PFWInjRvrtTms |  | unimplemented | RW
50302 | PFWInjRvrtRem |  | unimplemented | R
50304 | PFWAbsEna |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50305 | PFWAbsEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50306 | PFWAbsRvrtTms |  | unimplemented | RW
50308 | PFWAbsRvrtRem |  | unimplemented | R
50310 | WMaxLimPctEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50311 | WMaxLimPct |  | supported | RW | 0 | 100
50312 | WMaxLimPctRvrt |  | unimplemented | RW
50313 | WMaxLimPctEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50314 | WMaxLimPctRvrtTms |  | unimplemented | RW
50316 | WMaxLimPctRvrtRem |  | unimplemented | R
50318 | WSetEna |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50319 | WSetMod |  | unimplemented | RW
|  | W_MAX_PCT | unimplemented
|  | WATTS | unimplemented
50320 | WSet |  | supported | RW | 0 | 50000
50322 | WSetRvrt |  | supported | RW | 0 | 50000
50324 | WSetPct |  | supported | RW | 0 | 100
50325 | WSetPctRvrt |  | supported | RW | 0 | 100
50326 | WSetEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50327 | WSetRvrtTms |  | unimplemented | RW
50329 | WSetRvrtRem |  | unimplemented | R
50331 | VarSetEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50332 | VarSetMod |  | supported | RW
|  | W_MAX_PCT | supported
|  | VAR_MAX_PCT | supported
|  | VAR_AVAIL_PCT | supported
|  | VA_MAX_PCT | supported
|  | VARS | supported
50333 | VarSetPri |  | supported | RW
|  | ACTIVE | supported
|  | REACTIVE | supported
|  | VENDOR | supported
50334 | VarSet |  | supported | RW | -21794 | 21794
50336 | VarSetRvrt |  | supported | RW | -21794 | 21794
50338 | VarSetPct |  | supported | RW | -100 | 100
50339 | VarSetPctRvrt |  | supported | RW | -100 | 100
50340 | VarSetEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50341 | VarSetRvrtTms |  | unimplemented | RW
50343 | VarSetRvrtRem |  | unimplemented | R
50345 | WRmp |  | supported | RW | 0 | 1000
50346 | WRmpRef |  | supported | RW
|  | A_MAX | supported
|  | W_MAX | supported
50347 | VarRmp |  | unimplemented | RW
50348 | AntiIslEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50349 | PF_SF |  | -3 | R
50350 | WMaxLimPct_SF |  | 0 | R
50351 | WSet_SF |  | -2 | R
50352 | WSetPct_SF |  | -2 | R
50353 | VarSet_SF |  | -2 | R
50354 | VarSetPct_SF |  | 0 | R
50355 | PFWInj.PF |  | supported | RW | 0.85 | 1
50356 | PFWInj.Ext |  | supported | RW
|  | OVER_EXCITED | supported
|  | UNDER_EXCITED | supported
50357 | PFWInjRvrt.PF |  | unimplemented | RW
50358 | PFWInjRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented
50359 | PFWAbs.PF |  | unimplemented | RW
50360 | PFWAbs.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented
50361 | PFWAbsRvrt.PF |  | unimplemented | RW
50362 | PFWAbsRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented