## Instructions
DER Security Corp
IEEE-1547 Protocol Information Conformance Statement (PICS)
For manufacturers of DER devices that must comply with IEEE 1547-2018 and UL 1741 SB.
This file was generated by SunSpec Dashboard or DER Security LabTest software. It is used to prepare and submit a product for testing at a Nationally Recognized Testing Lab (for electrical function validation and certification) or a SunSpec Authorized Testing laboratory (for SunSpec Modbus and/or IEEE 2030.5 communication protocol validation and certification). Some data is input by the user into the SunSpec Dashboard or DER Security LabTest software prior to autogenerating this spreadsheet and some data is read from Equipment Under Test (EUT) by SunSpec Dashboard or DER Security LabTest software after the spreadsheet is generated.
The Product and Testing Info tab contains general information about the unit under test, the manufacturer of the product, and the test laboratory network setup. It also contains an area for test laboratory personnel to enter information about an IEEE 1547 test that has previously been run on the unit under test.
The Test Lab Settings tab contains information about the testing laboratory and test engineer that ran a test. Data is input to this tab by the test engineer after a test run is completed.
The IEEE 1547 Electrical Test Setup tab contains information needed to configure the EUT for electrical testing according the IEEE 1547.1 standard. Most parameters are defined in the IEEE 1547.1 "Test Requirements" section (section 5.14.2) and some were by DER Security Corp to facilitate electrical test setup.
Numerical Tab names refer to the specific SunSpec Modbus models contained in the EUT and tab names that start with "2030.5 CSIP-" refer to specific IEEE 2030.5 capabilities of the product that the EUT will be evaluated against.
DER Security Corp License Agreement and Copyright
This document and the information contained herein is provided on an "AS IS" basis and the DER Security Corp DISCLAIMS ALL WARRANTIES, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY WARRANTY THAT THE USE OF THE INFORMATION HEREIN WILL NOT INFRINGE ANY OWNERSHIP RIGHTS OR ANY IMPLIED WARRANTIES OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE.
This document may be used, copied, and furnished to others, without restrictions of any kind, provided that this document itself may not be modified in anyway, except as needed by the DER Security Corp Technical Committee and as governed by the DER Security Corp IPR Policy. The complete policy of DER Security Corp can be found at https://www.dersec.io/.

## Product and Testing Info
Product Information
Product Type | Inverter
Manufacturer Name | FOXESS CO., LTD.
Product Name | Inverter
Product Model Numbers | R75-G2, R80-G2, R100-G2, R110-G2, R125-G2, R136-G2, R125-K2
Submitter Information
Full Name | xueji dong
Job Title | Certifier
Company Name | CSA Group
Relationship to Manufacturer | Employee
Email | xueji.dong@csagroup.org
Phone
Device Under Test Information
Test Type | SunSpec Modbus Conformance Certification
Firmware Version Tested | V1.29
Firmware Checksum (in hex) | cde15e29949f905b681ee1e8fc84774d372eb0f7-00000008
Interface Type | RTU
If RTU
Interface Name | COM6
Unit ID | 1
Baud Rate | 9600
Parity | None
Timeout (secs) | 10
If Modbus TCP
IP Address
IP Port
Unit ID
If IEEE 2030.5
IP Address
IP Port
Poll Rate
Client PIN
Timeout (secs)
Reserved For SunSpec Alliance
SunSpec Certificate Number | SM-000060
Certificate Signer Name | Erin Mahan
Certificate Issued Date | 2026-08-07
Certificate Archive Location | https://sunspec.org/wp-content/uploads/2009/03/Certificate_FoxESS_SunSpec-Modbus_SM000060.pdf

## Test Lab Settings
Target Definition | Target Definition Label | Param | Param Label | Param Value

## IEEE 1547 Electrical Test Setup
Test Category | Param Definition | Param Definition Label | Param | Param Label | Param Unit | Param Value

## 1
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
2 | ID |  | 1 | R | 1 | 1
3 | L |  | 66 | R
4 | Mn |  | FOXESS CO.,LTD | R
20 | Md |  | R110-G2 | R
36 | Opt |  | RF114 | R
44 | Vr |  | 1.1.29.113 | R
52 | SN |  | 60RF114038EG003 | R
68 | DA |  | supported | RW | 0 | 247
69 | Pad |  | 0 | R

## 701
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
70 | ID |  | 701 | R | 701 | 701
71 | L |  | 153 | R
72 | ACType |  | supported | R
|  | SINGLE_PHASE | supported
|  | SPLIT_PHASE | supported
|  | THREE_PHASE | supported
73 | St |  | supported | R
|  | OFF | supported
|  | ON | supported
74 | InvSt |  | supported | R
|  | OFF | supported
|  | SLEEPING | supported
|  | STARTING | supported
|  | RUNNING | supported
|  | THROTTLED | supported
|  | SHUTTING_DOWN | supported
|  | FAULT | supported
|  | STANDBY | supported
75 | ConnSt |  | supported | R
|  | DISCONNECTED | supported
|  | CONNECTED | supported
76 | Alrm |  | supported | R
|  | GROUND_FAULT | supported
|  | DC_OVER_VOLT | supported
|  | AC_DISCONNECT | supported
|  | DC_DISCONNECT | supported
|  | GRID_DISCONNECT | supported
|  | CABINET_OPEN | supported
|  | MANUAL_SHUTDOWN | supported
|  | OVER_TEMP | supported
|  | OVER_FREQUENCY | supported
|  | UNDER_FREQUENCY | supported
|  | AC_OVER_VOLT | supported
|  | AC_UNDER_VOLT | supported
|  | BLOWN_STRING_FUSE | supported
|  | UNDER_TEMP | supported
|  | MEMORY_LOSS | supported
|  | HW_TEST_FAILURE | supported
|  | MANUFACTURER_ALRM | supported
78 | DERMode |  | unimplemented | R
|  | GRID_FOLLOWING | unimplemented
|  | GRID_FORMING | unimplemented
|  | PV_CLIPPED | unimplemented
80 | W |  | supported | R
81 | VA |  | supported | R
82 | Var |  | supported | R
83 | PF |  | supported | R
84 | A |  | unimplemented | R
85 | LLV |  | supported | R
86 | LNV |  | supported | R
87 | Hz |  | supported | R
89 | TotWhInj |  | unimplemented | R
93 | TotWhAbs |  | unimplemented | R
97 | TotVarhInj |  | unimplemented | R
101 | TotVarhAbs |  | unimplemented | R
105 | TmpAmb |  | unimplemented | R
106 | TmpCab |  | unimplemented | R
107 | TmpSnk |  | unimplemented | R
108 | TmpTrns |  | unimplemented | R
109 | TmpSw |  | unimplemented | R
110 | TmpOt |  | unimplemented | R
111 | WL1 |  | supported | R
112 | VAL1 |  | supported | R
113 | VarL1 |  | unimplemented | R
114 | PFL1 |  | unimplemented | R
115 | AL1 |  | supported | R
116 | VL1L2 |  | supported | R
117 | VL1 |  | supported | R
118 | TotWhInjL1 |  | unimplemented | R
122 | TotWhAbsL1 |  | unimplemented | R
126 | TotVarhInjL1 |  | unimplemented | R
130 | TotVarhAbsL1 |  | unimplemented | R
134 | WL2 |  | supported | R
135 | VAL2 |  | supported | R
136 | VarL2 |  | unimplemented | R
137 | PFL2 |  | unimplemented | R
138 | AL2 |  | supported | R
139 | VL2L3 |  | supported | R
140 | VL2 |  | supported | R
141 | TotWhInjL2 |  | unimplemented | R
145 | TotWhAbsL2 |  | unimplemented | R
149 | TotVarhInjL2 |  | unimplemented | R
153 | TotVarhAbsL2 |  | unimplemented | R
157 | WL3 |  | supported | R
158 | VAL3 |  | supported | R
159 | VarL3 |  | unimplemented | R
160 | PFL3 |  | unimplemented | R
161 | AL3 |  | supported | R
162 | VL3L1 |  | supported | R
163 | VL3 |  | supported | R
164 | TotWhInjL3 |  | unimplemented | R
168 | TotWhAbsL3 |  | unimplemented | R
172 | TotVarhInjL3 |  | unimplemented | R
176 | TotVarhAbsL3 |  | unimplemented | R
180 | ThrotPct |  | unimplemented | R
181 | ThrotSrc |  | unimplemented | R
|  | MAX_W | unimplemented
|  | FIXED_W | unimplemented
|  | FIXED_VAR | unimplemented
|  | FIXED_PF | unimplemented
|  | VOLT_VAR | unimplemented
|  | FREQ_WATT | unimplemented
|  | DYN_REACT_CURR | unimplemented
|  | LVRT | unimplemented
|  | HVRT | unimplemented
|  | WATT_VAR | unimplemented
|  | VOLT_WATT | unimplemented
|  | SCHEDULED | unimplemented
|  | LFRT | unimplemented
|  | HFRT | unimplemented
|  | DERATED | unimplemented
183 | A_SF |  | -1 | R
184 | V_SF |  | -1 | R
185 | Hz_SF |  | -2 | R
186 | W_SF |  | 2 | R
187 | PF_SF |  | -3 | R
188 | VA_SF |  | 2 | R
189 | Var_SF |  | 2 | R
190 | TotWh_SF |  | 2 | R
191 | TotVarh_SF |  | 2 | R
192 | Tmp_SF |  | -1 | R
193 | MnAlrmInfo |  | supported | R

## 702
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
225 | ID |  | 702 | R | 702 | 702
226 | L |  | 50 | R
227 | WMaxRtg |  | 1100 | R
228 | WOvrExtRtg |  | 880 | R
229 | WOvrExtRtgPF |  | 8 | R
230 | WUndExtRtg |  | 880 | R
231 | WUndExtRtgPF |  | 8 | R
232 | VAMaxRtg |  | 1210 | R
233 | VarMaxInjRtg |  | 660 | R
234 | VarMaxAbsRtg |  | 660 | R
235 | WChaRteMaxRtg |  | 1100 | R
236 | WDisChaRteMaxRtg |  | 1100 | R
237 | VAChaRteMaxRtg |  | 1210 | R
238 | VADisChaRteMaxRtg |  | 1210 | R
239 | VNomRtg |  | 2300 | R
240 | VMaxRtg |  | 2760 | R
241 | VMinRtg |  | 1840 | R
242 | AMaxRtg |  | 1594 | R
243 | PFOvrExtRtg |  | unimplemented | R
244 | PFUndExtRtg |  | unimplemented | R
245 | ReactSusceptRtg |  | 28 | R
246 | NorOpCatRtg |  | unimplemented | R
|  | CAT_A | unimplemented
|  | CAT_B | unimplemented
247 | AbnOpCatRtg |  | unimplemented | R
|  | CAT_1 | unimplemented
|  | CAT_2 | unimplemented
|  | CAT_3 | unimplemented
248 | CtrlModes |  | 16 | R
|  | MAX_W | supported
|  | FIXED_W | supported
|  | FIXED_VAR | supported
|  | FIXED_PF | supported
|  | VOLT_VAR | supported
|  | FREQ_WATT | supported
|  | DYN_REACT_CURR | supported
|  | LV_TRIP | supported
|  | HV_TRIP | supported
|  | WATT_VAR | supported
|  | VOLT_WATT | supported
|  | SCHEDULED | supported
|  | LF_TRIP | supported
|  | HF_TRIP | supported
250 | IntIslandCatRtg |  | unimplemented | R
|  | UNCATEGORIZED | unimplemented
|  | INT_ISL_CAPABLE | unimplemented
|  | BLACK_START_CAPABLE | unimplemented
|  | ISOCH_CAPABLE | unimplemented
251 | WMax |  | unimplemented | RW
252 | WMaxOvrExt |  | unimplemented | RW
253 | WOvrExtPF |  | unimplemented | RW
254 | WMaxUndExt |  | unimplemented | RW
255 | WUndExtPF |  | unimplemented | RW
256 | VAMax |  | unimplemented | RW
257 | VarMaxInj |  | unimplemented | RW
258 | VarMaxAbs |  | unimplemented | RW
259 | WChaRteMax |  | unimplemented | RW
260 | WDisChaRteMax |  | unimplemented | RW
261 | VAChaRteMax |  | unimplemented | RW
262 | VADisChaRteMax |  | unimplemented | RW
263 | VNom |  | unimplemented | RW
264 | VMax |  | unimplemented | RW
265 | VMin |  | unimplemented | RW
266 | AMax |  | unimplemented | RW
267 | PFOvrExt |  | unimplemented | RW
268 | PFUndExt |  | unimplemented | RW
269 | IntIslandCat |  | unimplemented | RW
|  | UNCATEGORIZED | unimplemented
|  | INT_ISL_CAPABLE | unimplemented
|  | BLACK_START_CAPABLE | unimplemented
|  | ISOCH_CAPABLE | unimplemented
270 | W_SF |  | 2 | R
271 | PF_SF |  | -1 | R
272 | VA_SF |  | 2 | R
273 | Var_SF |  | 2 | R
274 | V_SF |  | -1 | R
275 | A_SF |  | -1 | R
276 | S_SF |  | -5 | R

## 703
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
277 | ID |  | 703 | R | 703 | 703
278 | L |  | 17 | R
279 | ES |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
280 | ESVHi |  | supported | RW | 100 | 140
281 | ESVLo |  | supported | RW | 50 | 100
282 | ESHzHi |  | supported | RW | 50.2 | 55
284 | ESHzLo |  | supported | RW | 45 | 49.9
286 | ESDlyTms |  | supported | RW | 10 | 900
288 | ESRndTms |  | unimplemented | RW
290 | ESRmpTms |  | supported | RW | 1 | 1000
292 | ESDlyRemTms |  | unimplemented | R
294 | V_SF |  | -1 | R
295 | Hz_SF |  | -2 | R

## 704
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
296 | ID |  | 704 | R | 704 | 704
297 | L |  | 65 | R
298 | PFWInjEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
299 | PFWInjEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
300 | PFWInjRvrtTms |  | unimplemented | RW
302 | PFWInjRvrtRem |  | unimplemented | R
304 | PFWAbsEna |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
305 | PFWAbsEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
306 | PFWAbsRvrtTms |  | unimplemented | RW
308 | PFWAbsRvrtRem |  | unimplemented | R
310 | WMaxLimPctEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
311 | WMaxLimPct |  | supported | RW | 0 | 100
312 | WMaxLimPctRvrt |  | unimplemented | RW
313 | WMaxLimPctEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
314 | WMaxLimPctRvrtTms |  | unimplemented | RW
316 | WMaxLimPctRvrtRem |  | unimplemented | R
318 | WSetEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
319 | WSetMod |  | supported | RW
|  | W_MAX_PCT | supported
|  | WATTS | supported
320 | WSet |  | unimplemented | RW
322 | WSetRvrt |  | unimplemented | RW
324 | WSetPct |  | supported | RW | 0 | 100
325 | WSetPctRvrt |  | unimplemented | RW
326 | WSetEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
327 | WSetRvrtTms |  | unimplemented | RW
329 | WSetRvrtRem |  | unimplemented | R
331 | VarSetEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
332 | VarSetMod |  | supported | RW
|  | W_MAX_PCT | supported
|  | VAR_MAX_PCT | supported
|  | VAR_AVAIL_PCT | supported
|  | VA_MAX_PCT | supported
|  | VARS | supported
333 | VarSetPri |  | unimplemented | RW
|  | ACTIVE | unimplemented
|  | REACTIVE | unimplemented
|  | VENDOR | unimplemented
334 | VarSet |  | unimplemented | RW
336 | VarSetRvrt |  | unimplemented | RW
338 | VarSetPct |  | supported | RW | -100 | 100
339 | VarSetPctRvrt |  | unimplemented | RW
340 | VarSetEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
341 | VarSetRvrtTms |  | unimplemented | RW
343 | VarSetRvrtRem |  | unimplemented | R
345 | WRmp |  | supported | RW | 1 | 1000
346 | WRmpRef |  | supported | RW
|  | A_MAX | supported
|  | W_MAX | supported
347 | VarRmp |  | unimplemented | RW
348 | AntiIslEna |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
349 | PF_SF |  | -3 | R
350 | WMaxLimPct_SF |  | -1 | R
351 | WSet_SF |  | 2 | R
352 | WSetPct_SF |  | -1 | R
353 | VarSet_SF |  | 2 | R
354 | VarSetPct_SF |  | 0 | R
355 | PFWInj.PF |  | supported | RW | 0.85 | 1
356 | PFWInj.Ext |  | supported | RW
|  | OVER_EXCITED | supported
|  | UNDER_EXCITED | supported
357 | PFWInjRvrt.PF |  | unimplemented | RW
358 | PFWInjRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented
359 | PFWAbs.PF |  | unimplemented | RW
360 | PFWAbs.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented
361 | PFWAbsRvrt.PF |  | unimplemented | RW
362 | PFWAbsRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented

## 705
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
363 | ID |  | 705 | R | 705 | 705
364 | L |  | 49 | R
365 | Ena |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
366 | AdptCrvReq |  | supported | RW
367 | AdptCrvRslt |  | supported | R
|  | IN_PROGRESS | supported
|  | COMPLETED | supported
|  | FAILED | supported
368 | NPt |  | 4 | R
369 | NCrv |  | 2 | R
370 | RvrtTms |  | unimplemented | RW
372 | RvrtRem |  | unimplemented | R
374 | RvrtCrv |  | unimplemented | RW
375 | V_SF |  | -1 | R
376 | DeptRef_SF |  | -1 | R
377 | RspTms_SF |  | 0 | R
378 | Crv.1.ActPt |  | supported | RW | 4 | 4
379 | Crv.1.DeptRef |  | supported | RW
|  | W_MAX_PCT | supported
|  | VAR_MAX_PCT | supported
|  | VAR_AVAL_PCT | supported
|  | VA_MAX_PCT | supported
380 | Crv.1.Pri |  | supported | RW
|  | ACTIVE | supported
|  | REACTIVE | supported
|  | VENDOR | supported
381 | Crv.1.VRef |  | unimplemented | RW
382 | Crv.1.VRefAuto |  | unimplemented | R
383 | Crv.1.VRefAutoEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
384 | Crv.1.VRefAutoTms |  | supported | RW | 300 | 5000
385 | Crv.1.RspTms |  | supported | RW | 1 | 90
387 | Crv.1.ReadOnly |  | 1 | R
|  | RW | supported
|  | R | supported
388 | Crv.1.Pt.1.V |  | supported | RW | 77 | 98
389 | Crv.1.Pt.1.Var |  | supported | RW | 0 | 100
390 | Crv.1.Pt.2.V |  | supported | RW | 97 | 100
391 | Crv.1.Pt.2.Var |  | supported | RW | -100 | 100
392 | Crv.1.Pt.3.V |  | supported | RW | 100 | 103
393 | Crv.1.Pt.3.Var |  | supported | RW | -100 | 100
394 | Crv.1.Pt.4.V |  | supported | RW | 102 | 118
395 | Crv.1.Pt.4.Var |  | supported | RW | -100 | 0
396 | Crv.2.ActPt |  | supported | RW
397 | Crv.2.DeptRef |  | supported | RW
|  | W_MAX_PCT | supported
|  | VAR_MAX_PCT | supported
|  | VAR_AVAL_PCT | supported
|  | VA_MAX_PCT | supported
398 | Crv.2.Pri |  | supported | RW
|  | ACTIVE | supported
|  | REACTIVE | supported
|  | VENDOR | supported
399 | Crv.2.VRef |  | unimplemented | RW
400 | Crv.2.VRefAuto |  | unimplemented | R
401 | Crv.2.VRefAutoEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
402 | Crv.2.VRefAutoTms |  | supported | RW
403 | Crv.2.RspTms |  | supported | RW
405 | Crv.2.ReadOnly |  | 0 | R
|  | RW | supported
|  | R | supported
406 | Crv.2.Pt.1.V |  | supported | RW
407 | Crv.2.Pt.1.Var |  | supported | RW
408 | Crv.2.Pt.2.V |  | supported | RW
409 | Crv.2.Pt.2.Var |  | supported | RW
410 | Crv.2.Pt.3.V |  | supported | RW
411 | Crv.2.Pt.3.Var |  | supported | RW
412 | Crv.2.Pt.4.V |  | supported | RW
413 | Crv.2.Pt.4.Var |  | supported | RW

## 713
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
414 | ID |  | 713 | R | 713 | 713
415 | L |  | 7 | R
416 | WHRtg |  | unimplemented | R
417 | WHAvail |  | unimplemented | R
418 | SoC |  | unimplemented | R
419 | SoH |  | unimplemented | R
420 | Sta |  | unimplemented | R
|  | OK | unimplemented
|  | WARNING | unimplemented
|  | ERROR | unimplemented
421 | WH_SF |  | 1 | R
422 | Pct_SF |  | 0 | R

## 714
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
423 | ID |  | 714 | R | 714 | 714
424 | L |  | 268 | R
425 | PrtAlrms |  | unimplemented | R
427 | NPrt |  | 10 | R
428 | DCA |  | unimplemented | R
429 | DCW |  | supported | R
430 | DCWhInj |  | unimplemented | R
434 | DCWhAbs |  | unimplemented | R
438 | DCA_SF |  | -2 | R
439 | DCV_SF |  | -1 | R
440 | DCW_SF |  | 1 | R
441 | DCWH_SF |  | 1 | R
442 | Tmp_SF |  | -1 | R
443 | Prt.1.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
444 | Prt.1.ID |  | supported | R
445 | Prt.1.IDStr |  | supported | R
453 | Prt.1.DCA |  | supported | R
454 | Prt.1.DCV |  | supported | R
455 | Prt.1.DCW |  | supported | R
456 | Prt.1.DCWhInj |  | unimplemented | R
460 | Prt.1.DCWhAbs |  | unimplemented | R
464 | Prt.1.Tmp |  | unimplemented | R
465 | Prt.1.DCSta |  | unimplemented | R
|  | OFF | unimplemented
|  | ON | unimplemented
|  | WARNING | unimplemented
|  | ERROR | unimplemented
466 | Prt.1.DCAlrm |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | INPUT_OVER_VOLTAGE | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | BLOWN_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | ARC_DETECTION | unimplemented
|  | RESERVED | unimplemented
|  | TEST_FAILED | unimplemented
|  | INPUT_UNDER_VOLTAGE | unimplemented
|  | INPUT_OVER_CURRENT | unimplemented
468 | Prt.2.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
469 | Prt.2.ID |  | supported | R
470 | Prt.2.IDStr |  | supported | R
478 | Prt.2.DCA |  | supported | R
479 | Prt.2.DCV |  | supported | R
480 | Prt.2.DCW |  | supported | R
481 | Prt.2.DCWhInj |  | unimplemented | R
485 | Prt.2.DCWhAbs |  | unimplemented | R
489 | Prt.2.Tmp |  | unimplemented | R
490 | Prt.2.DCSta |  | unimplemented | R
|  | OFF | unimplemented
|  | ON | unimplemented
|  | WARNING | unimplemented
|  | ERROR | unimplemented
491 | Prt.2.DCAlrm |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | INPUT_OVER_VOLTAGE | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | BLOWN_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | ARC_DETECTION | unimplemented
|  | RESERVED | unimplemented
|  | TEST_FAILED | unimplemented
|  | INPUT_UNDER_VOLTAGE | unimplemented
|  | INPUT_OVER_CURRENT | unimplemented
493 | Prt.3.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
494 | Prt.3.ID |  | supported | R
495 | Prt.3.IDStr |  | supported | R
503 | Prt.3.DCA |  | supported | R
504 | Prt.3.DCV |  | supported | R
505 | Prt.3.DCW |  | supported | R
506 | Prt.3.DCWhInj |  | unimplemented | R
510 | Prt.3.DCWhAbs |  | unimplemented | R
514 | Prt.3.Tmp |  | unimplemented | R
515 | Prt.3.DCSta |  | unimplemented | R
|  | OFF | unimplemented
|  | ON | unimplemented
|  | WARNING | unimplemented
|  | ERROR | unimplemented
516 | Prt.3.DCAlrm |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | INPUT_OVER_VOLTAGE | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | BLOWN_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | ARC_DETECTION | unimplemented
|  | RESERVED | unimplemented
|  | TEST_FAILED | unimplemented
|  | INPUT_UNDER_VOLTAGE | unimplemented
|  | INPUT_OVER_CURRENT | unimplemented
518 | Prt.4.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
519 | Prt.4.ID |  | supported | R
520 | Prt.4.IDStr |  | supported | R
528 | Prt.4.DCA |  | supported | R
529 | Prt.4.DCV |  | supported | R
530 | Prt.4.DCW |  | supported | R
531 | Prt.4.DCWhInj |  | unimplemented | R
535 | Prt.4.DCWhAbs |  | unimplemented | R
539 | Prt.4.Tmp |  | unimplemented | R
540 | Prt.4.DCSta |  | unimplemented | R
|  | OFF | unimplemented
|  | ON | unimplemented
|  | WARNING | unimplemented
|  | ERROR | unimplemented
541 | Prt.4.DCAlrm |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | INPUT_OVER_VOLTAGE | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | BLOWN_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | ARC_DETECTION | unimplemented
|  | RESERVED | unimplemented
|  | TEST_FAILED | unimplemented
|  | INPUT_UNDER_VOLTAGE | unimplemented
|  | INPUT_OVER_CURRENT | unimplemented
543 | Prt.5.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
544 | Prt.5.ID |  | supported | R
545 | Prt.5.IDStr |  | supported | R
553 | Prt.5.DCA |  | supported | R
554 | Prt.5.DCV |  | supported | R
555 | Prt.5.DCW |  | supported | R
556 | Prt.5.DCWhInj |  | unimplemented | R
560 | Prt.5.DCWhAbs |  | unimplemented | R
564 | Prt.5.Tmp |  | unimplemented | R
565 | Prt.5.DCSta |  | unimplemented | R
|  | OFF | unimplemented
|  | ON | unimplemented
|  | WARNING | unimplemented
|  | ERROR | unimplemented
566 | Prt.5.DCAlrm |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | INPUT_OVER_VOLTAGE | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | BLOWN_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | ARC_DETECTION | unimplemented
|  | RESERVED | unimplemented
|  | TEST_FAILED | unimplemented
|  | INPUT_UNDER_VOLTAGE | unimplemented
|  | INPUT_OVER_CURRENT | unimplemented
568 | Prt.6.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
569 | Prt.6.ID |  | supported | R
570 | Prt.6.IDStr |  | supported | R
578 | Prt.6.DCA |  | supported | R
579 | Prt.6.DCV |  | supported | R
580 | Prt.6.DCW |  | supported | R
581 | Prt.6.DCWhInj |  | unimplemented | R
585 | Prt.6.DCWhAbs |  | unimplemented | R
589 | Prt.6.Tmp |  | unimplemented | R
590 | Prt.6.DCSta |  | unimplemented | R
|  | OFF | unimplemented
|  | ON | unimplemented
|  | WARNING | unimplemented
|  | ERROR | unimplemented
591 | Prt.6.DCAlrm |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | INPUT_OVER_VOLTAGE | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | BLOWN_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | ARC_DETECTION | unimplemented
|  | RESERVED | unimplemented
|  | TEST_FAILED | unimplemented
|  | INPUT_UNDER_VOLTAGE | unimplemented
|  | INPUT_OVER_CURRENT | unimplemented
593 | Prt.7.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
594 | Prt.7.ID |  | supported | R
595 | Prt.7.IDStr |  | supported | R
603 | Prt.7.DCA |  | supported | R
604 | Prt.7.DCV |  | supported | R
605 | Prt.7.DCW |  | supported | R
606 | Prt.7.DCWhInj |  | unimplemented | R
610 | Prt.7.DCWhAbs |  | unimplemented | R
614 | Prt.7.Tmp |  | unimplemented | R
615 | Prt.7.DCSta |  | unimplemented | R
|  | OFF | unimplemented
|  | ON | unimplemented
|  | WARNING | unimplemented
|  | ERROR | unimplemented
616 | Prt.7.DCAlrm |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | INPUT_OVER_VOLTAGE | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | BLOWN_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | ARC_DETECTION | unimplemented
|  | RESERVED | unimplemented
|  | TEST_FAILED | unimplemented
|  | INPUT_UNDER_VOLTAGE | unimplemented
|  | INPUT_OVER_CURRENT | unimplemented
618 | Prt.8.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
619 | Prt.8.ID |  | supported | R
620 | Prt.8.IDStr |  | supported | R
628 | Prt.8.DCA |  | supported | R
629 | Prt.8.DCV |  | supported | R
630 | Prt.8.DCW |  | supported | R
631 | Prt.8.DCWhInj |  | unimplemented | R
635 | Prt.8.DCWhAbs |  | unimplemented | R
639 | Prt.8.Tmp |  | unimplemented | R
640 | Prt.8.DCSta |  | unimplemented | R
|  | OFF | unimplemented
|  | ON | unimplemented
|  | WARNING | unimplemented
|  | ERROR | unimplemented
641 | Prt.8.DCAlrm |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | INPUT_OVER_VOLTAGE | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | BLOWN_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | ARC_DETECTION | unimplemented
|  | RESERVED | unimplemented
|  | TEST_FAILED | unimplemented
|  | INPUT_UNDER_VOLTAGE | unimplemented
|  | INPUT_OVER_CURRENT | unimplemented
643 | Prt.9.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
644 | Prt.9.ID |  | supported | R
645 | Prt.9.IDStr |  | supported | R
653 | Prt.9.DCA |  | supported | R
654 | Prt.9.DCV |  | supported | R
655 | Prt.9.DCW |  | supported | R
656 | Prt.9.DCWhInj |  | unimplemented | R
660 | Prt.9.DCWhAbs |  | unimplemented | R
664 | Prt.9.Tmp |  | unimplemented | R
665 | Prt.9.DCSta |  | unimplemented | R
|  | OFF | unimplemented
|  | ON | unimplemented
|  | WARNING | unimplemented
|  | ERROR | unimplemented
666 | Prt.9.DCAlrm |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | INPUT_OVER_VOLTAGE | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | BLOWN_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | ARC_DETECTION | unimplemented
|  | RESERVED | unimplemented
|  | TEST_FAILED | unimplemented
|  | INPUT_UNDER_VOLTAGE | unimplemented
|  | INPUT_OVER_CURRENT | unimplemented
668 | Prt.10.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
669 | Prt.10.ID |  | supported | R
670 | Prt.10.IDStr |  | supported | R
678 | Prt.10.DCA |  | supported | R
679 | Prt.10.DCV |  | supported | R
680 | Prt.10.DCW |  | supported | R
681 | Prt.10.DCWhInj |  | unimplemented | R
685 | Prt.10.DCWhAbs |  | unimplemented | R
689 | Prt.10.Tmp |  | unimplemented | R
690 | Prt.10.DCSta |  | unimplemented | R
|  | OFF | unimplemented
|  | ON | unimplemented
|  | WARNING | unimplemented
|  | ERROR | unimplemented
691 | Prt.10.DCAlrm |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | INPUT_OVER_VOLTAGE | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | BLOWN_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | ARC_DETECTION | unimplemented
|  | RESERVED | unimplemented
|  | TEST_FAILED | unimplemented
|  | INPUT_UNDER_VOLTAGE | unimplemented
|  | INPUT_OVER_CURRENT | unimplemented

## 715
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
693 | ID |  | 715 | R
694 | L |  | 7 | R
695 | LocRemCtl |  | unimplemented | R
|  | REMOTE | unimplemented
|  | LOCAL | unimplemented
696 | DERHb |  | unimplemented | R
698 | ControllerHb |  | unimplemented | RW
700 | AlarmReset |  | unimplemented | RW
701 | OpCtl |  | supported | RW
|  | STOP | supported
|  | START | supported
|  | ENTER_STANDBY | supported
|  | EXIT_STANDBY | supported