## Instructions
SunSpec PICS
This SunSpec PICS was generated by SunSpec Dashboard v3.8.2 based on the model contents of the connected device.
Most of the necessary information is populated but the PICS must be completed before submission by performing the following steps:
1. Examine the entry in the 'Value' column for each point to verify correctness:
- Common model (1) points that are implemented should contain the current value.
- All other model points that are implemented and have a variable value should contain the string 'supported'.
- All other model points that are implemented and have a constant value should contain the constant value.
It is assumed that scale factors are constants. If they are not, change the value to 'supported'.
- All unimplemented points should contain the string 'unimplemented'.
- For each enumeration or bit field entry that is not implemented, change the string to 'unimplemented'.
2. Examine the 'R/W' column to ensure the access is correct. It should be either 'R' or 'RW'.
3. Some points require a value range be specified. Points that have a grey background in the Min and Max column must
have a minimum and maximum value specified in the Min and Max columns. The value should be the value with the scale
factor applied. For example, a value specified in these fields would be 97.34 not 9734 if the scale factor is -2.
For models that have repeating elements, the value range is specified on the points in the first element and are
applicable for all of the repeating elements.
4. For any point that has an implementation deviation or special considerations indicate the issue in the 'Conformance Notes' column.
The certificate number will be filled in when certification is complete and this file will be archived with the Testing Info tab removed
along with a copy of the certificate on sunspec.org.

## Product and Testing Info
Product Information
Product Type | Gateway
Manufacturer Name | Atmoce Holding B.V.
Product Name | M-Gateway
Product Model Numbers | MG100, MG100-Wye, MG100-Delta
Submitter Information
Full Name | Xu Bin
Job Title | Quality & Test Director
Company Name | MG100-Wye
Relationship to Manufacturer | Employee
Email | xubin@moorewatt.com
Phone | +86 17712776969
Device Under Test Information
Test Type | SunSpec Modbus Conformance Certification
Firmware Version Tested | 01.01.00
Firmware Checksum (in hex) | 45CE4F756459D10202D492D2C543834E6D49961433303060641BFA56E9F36853
Interface Type | RTU
If RTU
Interface Name | COM12
Unit ID | 1
Baud Rate | 9600
Parity | None
Timeout (secs) | 1
If Modbus TCP
IP Address
IP Port
Unit ID
If IEEE 2030.5
IP Address
IP Port
Poll Rate
Client PIN
Timeout (secs)
Reserved For SunSpec Alliance
SunSpec Certificate Number | SM-000063
Certificate Signer Name | Erin Mahan
Certificate Issued Date | 2026-09-30
Certificate Archive Location | https://sunspec.org/wp-content/uploads/2009/03/Atmoce_Modbus_Certificate_SM000063.pdf

## Test Lab Settings
Target Definition | Target Definition Label | Param | Param Label | Param Value

## IEEE 1547 Electrical Test Setup
Test Category | Param Definition | Param Definition Label | Param | Param Label | Param Unit | Param Value

## 1
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40002 | ID |  | 1 | R | 1 | 1
40003 | L |  | 66 | R
40004 | Mn |  | Atmoce | R
40020 | Md |  | MG100-Wye | R
40036 | Opt |  | unimplemented | R
40044 | Vr |  | 01.01.00.29.62 | R
40052 | SN |  | ES268224BAC | R
40068 | DA |  | supported | RW | 1 | 247
40069 | Pad |  | 32768 | R

## 703
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40070 | ID |  | 703 | R | 703 | 703
40071 | L |  | 17 | R
40072 | ES |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40073 | ESVHi |  | unimplemented | RW
40074 | ESVLo |  | unimplemented | RW
40075 | ESHzHi |  | unimplemented | RW
40077 | ESHzLo |  | unimplemented | RW
40079 | ESDlyTms |  | unimplemented | RW
40081 | ESRndTms |  | unimplemented | RW
40083 | ESRmpTms |  | unimplemented | RW
40085 | ESDlyRemTms |  | unimplemented | R
40087 | V_SF |  | unimplemented | R
40088 | Hz_SF |  | unimplemented | R

## 704
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40089 | ID |  | 704 | R | 704 | 704
40090 | L |  | 65 | R
40091 | PFWInjEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40092 | PFWInjEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40093 | PFWInjRvrtTms |  | unimplemented | RW
40095 | PFWInjRvrtRem |  | unimplemented | R
40097 | PFWAbsEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40098 | PFWAbsEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40099 | PFWAbsRvrtTms |  | unimplemented | RW
40101 | PFWAbsRvrtRem |  | unimplemented | R
40103 | WMaxLimPctEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40104 | WMaxLimPct |  | supported | RW | 0 | 100
40105 | WMaxLimPctRvrt |  | unimplemented | RW
40106 | WMaxLimPctEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40107 | WMaxLimPctRvrtTms |  | unimplemented | RW
40109 | WMaxLimPctRvrtRem |  | unimplemented | R
40111 | WSetEna |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40112 | WSetMod |  | unimplemented | RW
|  | W_MAX_PCT | unimplemented
|  | WATTS | unimplemented
40113 | WSet |  | unimplemented | RW
40115 | WSetRvrt |  | unimplemented | RW
40117 | WSetPct |  | unimplemented | RW
40118 | WSetPctRvrt |  | unimplemented | RW
40119 | WSetEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40120 | WSetRvrtTms |  | unimplemented | RW
40122 | WSetRvrtRem |  | unimplemented | R
40124 | VarSetEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40125 | VarSetMod |  | supported | RW
|  | W_MAX_PCT | unimplemented
|  | VAR_MAX_PCT | supported
|  | VAR_AVAIL_PCT | unimplemented
|  | VA_MAX_PCT | unimplemented
|  | VARS | supported
40126 | VarSetPri |  | unimplemented | RW
|  | ACTIVE | unimplemented
|  | REACTIVE | unimplemented
|  | VENDOR | unimplemented
40127 | VarSet |  | supported | RW | -6000 | 6000
40129 | VarSetRvrt |  | unimplemented | RW
40131 | VarSetPct |  | supported | RW | -100 | 100
40132 | VarSetPctRvrt |  | unimplemented | RW
40133 | VarSetEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40134 | VarSetRvrtTms |  | unimplemented | RW
40136 | VarSetRvrtRem |  | unimplemented | R
40138 | WRmp |  | unimplemented | RW
40139 | WRmpRef |  | unimplemented | RW
|  | A_MAX | unimplemented
|  | W_MAX | unimplemented
40140 | VarRmp |  | unimplemented | RW
40141 | AntiIslEna |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40142 | PF_SF |  | -3 | R
40143 | WMaxLimPct_SF |  | -1 | R
40144 | WSet_SF |  | unimplemented | R
40145 | WSetPct_SF |  | unimplemented | R
40146 | VarSet_SF |  | -1 | R
40147 | VarSetPct_SF |  | -1 | R
40148 | PFWInj.PF |  | supported | RW | 0.8 | 1
40149 | PFWInj.Ext |  | supported | RW
|  | OVER_EXCITED | supported
|  | UNDER_EXCITED | supported
40150 | PFWInjRvrt.PF |  | unimplemented | RW
40151 | PFWInjRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented
40152 | PFWAbs.PF |  | supported | RW | 0.8 | 1
40153 | PFWAbs.Ext |  | supported | RW
|  | OVER_EXCITED | supported
|  | UNDER_EXCITED | supported
40154 | PFWAbsRvrt.PF |  | unimplemented | RW
40155 | PFWAbsRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented