## Instructions
SunSpec PICS
This SunSpec PICS was generated by SunSpec Dashboard v3.8.2 based on the model contents of the connected device.
Most of the necessary information is populated but the PICS must be completed before submission by performing the following steps:
1. Examine the entry in the 'Value' column for each point to verify correctness:
- Common model (1) points that are implemented should contain the current value.
- All other model points that are implemented and have a variable value should contain the string 'supported'.
- All other model points that are implemented and have a constant value should contain the constant value.
It is assumed that scale factors are constants. If they are not, change the value to 'supported'.
- All unimplemented points should contain the string 'unimplemented'.
- For each enumeration or bit field entry that is not implemented, change the string to 'unimplemented'.
2. Examine the 'R/W' column to ensure the access is correct. It should be either 'R' or 'RW'.
3. Some points require a value range be specified. Points that have a grey background in the Min and Max column must
have a minimum and maximum value specified in the Min and Max columns. The value should be the value with the scale
factor applied. For example, a value specified in these fields would be 97.34 not 9734 if the scale factor is -2.
For models that have repeating elements, the value range is specified on the points in the first element and are
applicable for all of the repeating elements.
4. For any point that has an implementation deviation or special considerations indicate the issue in the 'Conformance Notes' column.
The certificate number will be filled in when certification is complete and this file will be archived with the Testing Info tab removed
along with a copy of the certificate on sunspec.org.

## Product and Testing Info
Product Information
Product Type | Inverter
Manufacturer Name | Shenzhen Sinexcel Isuna Energy Technology Co., Ltd.
Product Name | Hybrid Inverter
Product Model Numbers | Isuna L22K-TH-S, Isuna L25K-TH-S, Isuna L29.9K-TH-S, Isuna L30K-TH-S, Isuna L40K-TH-S, Isuna L42.5K-TH-S, Isuna L50K-TH-S, Isuna L22K-TH, Isuna L25K-TH, Isuna L29.9K-TH, Isuna L30K-TH, Isuna L40K-TH, Isuna L42.5K-TH, Isuna L50K-TH Isuna D5K-SL-S, Isuna D6K-SL-S, Isuna D8K-SL-S, Isuna D9.9K-SL-S, Isuna D10K-SL-S, Isuna D12K-SL-S, Isuna D5K-SL, Isuna D6K-SL, Isuna D8K-SL, Isuna D9.9K-SL, Isuna D10K-SL, Isuna D12K-SL, Isuna D5K-SH, Isuna D6K-SH, Isuna D8K-SH, Isuna D9.9K-SH, Isuna D10K-SH, Isuna D12K-SH Isuna D5K-TL-S, Isuna D6K-TL-S, Isuna D8K-TL-S, Isuna D9.9K-TL-S, Isuna D10K-TL-S, Isuna D12K-TL-S, Isuna D5K-TL, Isuna D6K-TL, Isuna D8K-TL, Isuna D9.9K-TL, Isuna D10K-TL, Isuna D12K-TL, Isuna D5K-TH, Isuna D6K-TH, Isuna D8K-TH, Isuna D9.9K-TH, Isuna D10K-TH, Isuna D12K-TH Isuna 3000S, Isuna 3600S, Isuna 4000S, Isuna 4600S, Isuna 5000S, Isuna 6000S Isuna 5000T, Isuna 6000T, Isuna 8000T, Isuna 10000T, Isuna 12000T, Isuna 15000T, Isuna 18000T, Isuna 20000T
Submitter Information
Full Name | Qiujie Zhang
Job Title | Certification Engineer
Company Name | Shenzhen Sinexcel Isuna Energy Technology Co., Ltd.
Relationship to Manufacturer | Employee
Email | qiujie_zhang@sinexcel.com
Phone | (+86) 0755 86511588
Device Under Test Information
Test Type | SunSpec Modbus Conformance Certification
Firmware Version Tested | V100
Firmware Checksum (in hex) | edd8c5a173a0d8fa9fd3a6379f93dc136c0c2763ce5ff17e93728e5ef5206b59
Interface Type | RTU
If RTU
Interface Name | COM12
Unit ID | 1
Baud Rate | 115200
Parity | None
Timeout (secs) | 1
If Modbus TCP
IP Address
IP Port
Unit ID
If IEEE 2030.5
IP Address
IP Port
Poll Rate
Client PIN
Timeout (secs)
Reserved For SunSpec Alliance
SunSpec Certificate Number | SM-000061
Certificate Signer Name | Erin Mahan
Certificate Issued Date | Tuesday, August 19, 2026
Certificate Archive Location | https://sunspec.org/wp-content/uploads/2009/03/Updated-Certificate_Sinexcel-Isuna_SunSpec-Modbus_SM000061.pdf

## Test Lab Settings
Target Definition | Target Definition Label | Param | Param Label | Param Value

## IEEE 1547 Electrical Test Setup
Test Category | Param Definition | Param Definition Label | Param | Param Label | Param Unit | Param Value

## 1
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
2 | ID |  | 1 | R | 1 | 1
3 | L |  | 66 | R
4 | Mn |  | Sinexcel Isuna | R
20 | Md |  | Isuna L50K-TH | R
36 | Opt |  | unimplemented | R
44 | Vr |  | V100 | R
52 | SN |  | E026A0005 | R
68 | DA |  | supported | RW | 1 | 247
69 | Pad |  | 32768 | R

## 703
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
70 | ID |  | 703 | R | 703 | 703
71 | L |  | 17 | R
72 | ES |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
73 | ESVHi |  | supported | RW | 100 | 130
74 | ESVLo |  | supported | RW | 50 | 100
75 | ESHzHi |  | supported | RW | 50 | 60
77 | ESHzLo |  | supported | RW | 35 | 50
79 | ESDlyTms |  | supported | RW | 0 | 1000
81 | ESRndTms |  | supported | RW | 0 | 1200
83 | ESRmpTms |  | supported | RW | 60 | 6000
85 | ESDlyRemTms |  | unimplemented | R
87 | V_SF |  | -2 | R
88 | Hz_SF |  | -2 | R

## 704
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
89 | ID |  | 704 | R | 704 | 704
90 | L |  | 65 | R
91 | PFWInjEna |  | supported | RW
|  | DISABLED | unimplemented
|  | ENABLED | supported
92 | PFWInjEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
93 | PFWInjRvrtTms |  | unimplemented | RW
95 | PFWInjRvrtRem |  | unimplemented | R
97 | PFWAbsEna |  | supported | RW
|  | DISABLED | unimplemented
|  | ENABLED | supported
98 | PFWAbsEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
99 | PFWAbsRvrtTms |  | unimplemented | RW
101 | PFWAbsRvrtRem |  | unimplemented | R
103 | WMaxLimPctEna |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
104 | WMaxLimPct |  | unimplemented | RW
105 | WMaxLimPctRvrt |  | unimplemented | RW
106 | WMaxLimPctEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
107 | WMaxLimPctRvrtTms |  | unimplemented | RW
109 | WMaxLimPctRvrtRem |  | unimplemented | R
111 | WSetEna |  | supported | RW
|  | DISABLED | unimplemented
|  | ENABLED | supported
112 | WSetMod |  | supported | RW
|  | W_MAX_PCT | supported
|  | WATTS | supported
113 | WSet |  | supported | RW | 0 | 50000
115 | WSetRvrt |  | unimplemented | RW
117 | WSetPct |  | supported | RW | 0 | 100
118 | WSetPctRvrt |  | unimplemented | RW
119 | WSetEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
120 | WSetRvrtTms |  | unimplemented | RW
122 | WSetRvrtRem |  | unimplemented | R
124 | VarSetEna |  | supported | RW
|  | DISABLED | unimplemented
|  | ENABLED | supported
125 | VarSetMod |  | supported | RW
|  | W_MAX_PCT | supported
|  | VAR_MAX_PCT | unimplemented
|  | VAR_AVAIL_PCT | unimplemented
|  | VA_MAX_PCT | unimplemented
|  | VARS | supported
126 | VarSetPri |  | unimplemented | RW
|  | ACTIVE | unimplemented
|  | REACTIVE | unimplemented
|  | VENDOR | unimplemented
127 | VarSet |  | supported | RW | 0 | 50000
129 | VarSetRvrt |  | unimplemented | RW
131 | VarSetPct |  | supported | RW | 0 | 100
132 | VarSetPctRvrt |  | unimplemented | RW
133 | VarSetEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
134 | VarSetRvrtTms |  | unimplemented | RW
136 | VarSetRvrtRem |  | unimplemented | R
138 | WRmp |  | supported | RW | 0 | 10000
139 | WRmpRef |  | unimplemented | RW
|  | A_MAX | unimplemented
|  | W_MAX | unimplemented
140 | VarRmp |  | unimplemented | RW
141 | AntiIslEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
142 | PF_SF |  | -2 | R
143 | WMaxLimPct_SF |  | -2 | R
144 | WSet_SF |  | -2 | R
145 | WSetPct_SF |  | -2 | R
146 | VarSet_SF |  | -2 | R
147 | VarSetPct_SF |  | -2 | R
148 | PFWInj.PF |  | supported | RW | 0 | 1
149 | PFWInj.Ext |  | supported | RW
|  | OVER_EXCITED | supported
|  | UNDER_EXCITED | supported
150 | PFWInjRvrt.PF |  | unimplemented | RW
151 | PFWInjRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented
152 | PFWAbs.PF |  | supported | RW | 0 | 1
153 | PFWAbs.Ext |  | supported | RW
|  | OVER_EXCITED | supported
|  | UNDER_EXCITED | supported
154 | PFWAbsRvrt.PF |  | unimplemented | RW
155 | PFWAbsRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented