## Instructions
DER Security Corp
IEEE-1547 Protocol Information Conformance Statement (PICS)
For manufacturers of DER devices that must comply with IEEE 1547-2018 and UL 1741 SB.
This file was generated by SunSpec Dashboard or DER Security LabTest software. It is used to prepare and submit a product for testing at a Nationally Recognized Testing Lab (for electrical function validation and certification) or a SunSpec Authorized Testing laboratory (for SunSpec Modbus and/or IEEE 2030.5 communication protocol validation and certification). Some data is input by the user into the SunSpec Dashboard or DER Security LabTest software prior to autogenerating this spreadsheet and some data is read from Equipment Under Test (EUT) by SunSpec Dashboard or DER Security LabTest software after the spreadsheet is generated.
The Product and Testing Info tab contains general information about the unit under test, the manufacturer of the product, and the test laboratory network setup. It also contains an area for test laboratory personnel to enter information about an IEEE 1547 test that has previously been run on the unit under test.
The Test Lab Settings tab contains information about the testing laboratory and test engineer that ran a test. Data is input to this tab by the test engineer after a test run is completed.
The IEEE 1547 Electrical Test Setup tab contains information needed to configure the EUT for electrical testing according the IEEE 1547.1 standard. Most parameters are defined in the IEEE 1547.1 "Test Requirements" section (section 5.14.2) and some were by DER Security Corp to facilitate electrical test setup.
Numerical Tab names refer to the specific SunSpec Modbus models contained in the EUT and tab names that start with "2030.5 CSIP-" refer to specific IEEE 2030.5 capabilities of the product that the EUT will be evaluated against.
DER Security Corp License Agreement and Copyright
This document and the information contained herein is provided on an "AS IS" basis and the DER Security Corp DISCLAIMS ALL WARRANTIES, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY WARRANTY THAT THE USE OF THE INFORMATION HEREIN WILL NOT INFRINGE ANY OWNERSHIP RIGHTS OR ANY IMPLIED WARRANTIES OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE.
This document may be used, copied, and furnished to others, without restrictions of any kind, provided that this document itself may not be modified in anyway, except as needed by the DER Security Corp Technical Committee and as governed by the DER Security Corp IPR Policy. The complete policy of DER Security Corp can be found at https://www.dersec.io/.

## Product and Testing Info
Product Information
Product Type | Inverter
Manufacturer Name | SigenergyTechnology Co.,Ltd.
Product Name | Sigen Inverter
Product Model Numbers | SigenStor Neo EC 2.5 SP, SigenStor Neo EC 3.0 SP, SigenStor Neo EC 3.6 SP, SigenStor Neo EC 4.0 SP, SigenStor Neo EC 4.6 SP, SigenStor Neo EC 5.0 SP, SigenStor Neo EC 6.0 SP, SigenStor Neo EC 8.0 SP, SigenStor Neo EC 10.0 SP, SigenStor Neo EC 12.0 SP, SigenStor Neo EC 3.0 TP, SigenStor Neo EC 4.0 TP, SigenStor Neo EC 5.0 TP, SigenStor Neo EC 6.0 TP, SigenStor Neo EC 8.0 TP, SigenStor Neo EC 10.0 TP, SigenStor Neo EC 12.0 TP, SigenStor Neo EC 15.0 TP, SigenStor Neo EC 2.5 SP AU, SigenStor Neo EC 3.0 SP AU, SigenStor Neo EC 3.6 SP AU, SigenStor Neo EC 4.0 SP AU, SigenStor Neo EC 4.6 SP AU, SigenStor Neo EC 5.0 SP AU, SigenStor Neo EC 6.0 SP AU, SigenStor Neo EC 8.0 SP AU, SigenStor Neo EC 10.0 SP AU, SigenStor Neo EC 12.0 SP AU, SigenStor Neo EC 3.0 TP AU, SigenStor Neo EC 4.0 TP AU, SigenStor Neo EC 5.0 TP AU, SigenStor Neo EC 6.0 TP AU, SigenStor Neo EC 8.0 TP AU, SigenStor Neo EC 10.0 TP AU, SigenStor Neo EC 12.0 TP AU, SigenStor Neo EC 15.0 TP AU, SigenStor Neo-2.5S, SigenStor Neo-3.0S, SigenStor Neo-3.6S, SigenStor Neo-4.0S, SigenStor Neo-4.6S, SigenStor Neo-5.0S, SigenStor Neo-6.0S, SigenStor Neo-8.0S, SigenStor Neo-10.0S, SigenStor Neo-12.0S, SigenStor Neo-3.0T, SigenStor Neo-4.0T, SigenStor Neo-5.0T, SigenStor Neo-6.0T, SigenStor Neo-8.0T, SigenStor Neo-10.0T, SigenStor Neo-12.0T, SigenStor Neo-15.0T, SigenStor Neo EC 2.5 SE SP, SigenStor Neo EC 3.0 SE SP, SigenStor Neo EC 3.6 SE SP, SigenStor Neo EC 4.0 SE SP, SigenStor Neo EC 4.6 SE SP, SigenStor Neo EC 5.0 SE SP, SigenStor Neo EC 6.0 SE SP, SigenStor Neo EC 2.5 SE SP AU, SigenStor Neo EC 3.0 SE SP AU, SigenStor Neo EC 3.6 SE SP AU, SigenStor Neo EC 5.0 SE SP AU, SigenStor Neo EC 6.0 SE SP AU
Submitter Information
Full Name | xueji dong
Job Title
Company Name | csa
Relationship to Manufacturer | Employee
Email | xueji.dong@csagroup.org
Phone
Device Under Test Information
Test Type | SunSpec Modbus Conformance Certification
Firmware Version Tested | V100R001
Firmware Checksum (in hex) | 482c456adc93bb38d95f32738b0c11d3
Interface Type | Modbus TCP, RTU
If RTU
Interface Name | COM4
Unit ID | 1
Baud Rate | 9600
Parity | None
Timeout (secs) | 15
If Modbus TCP
IP Address | 192.168.0.188
IP Port | 502
Unit ID | 1
If IEEE 2030.5
IP Address
IP Port
Poll Rate
Client PIN
Timeout (secs)
Reserved For SunSpec Alliance
SunSpec Certificate Number | SM-000055
Certificate Signer Name | Erin Mahan
Certificate Issued Date | June 11 2026
Certificate Archive Location | https://sunspec.org/wp-content/uploads/2009/03/Sigenergy_Modbus_Certificate_SM000055.pdf

## Test Lab Settings
Target Definition | Target Definition Label | Param | Param Label | Param Value

## IEEE 1547 Electrical Test Setup
Test Category | Param Definition | Param Definition Label | Param | Param Label | Param Unit | Param Value

## 1
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40002 | ID |  | 1 | R | 1 | 1
40003 | L |  | 66 | R
40004 | Mn |  | Sigenergy | R
40020 | Md |  | SigenStor Neo EC 12.0 SP | R
40036 | Opt |  | unimplemented | R
40044 | Vr |  | V100R001 | R
40052 | SN |  | CMUNEO123456789 | R
40068 | DA |  | supported | RW | 0 | 247
40069 | Pad |  | 0 | R

## 704
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40070 | ID |  | 704 | R | 704 | 704
40071 | L |  | 65 | R
40072 | PFWInjEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40073 | PFWInjEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40074 | PFWInjRvrtTms |  | unimplemented | RW
40076 | PFWInjRvrtRem |  | unimplemented | R
40078 | PFWAbsEna |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40079 | PFWAbsEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40080 | PFWAbsRvrtTms |  | unimplemented | RW
40082 | PFWAbsRvrtRem |  | unimplemented | R
40084 | WMaxLimPctEna |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40085 | WMaxLimPct |  | unimplemented | RW
40086 | WMaxLimPctRvrt |  | unimplemented | RW
40087 | WMaxLimPctEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40088 | WMaxLimPctRvrtTms |  | unimplemented | RW
40090 | WMaxLimPctRvrtRem |  | unimplemented | R
40092 | WSetEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40093 | WSetMod |  | supported | RW
|  | W_MAX_PCT | supported
|  | WATTS | supported
40094 | WSet |  | supported | RW | 0 | 12000
40096 | WSetRvrt |  | unimplemented | RW
40098 | WSetPct |  | supported | RW | 0 | 100
40099 | WSetPctRvrt |  | unimplemented | RW
40100 | WSetEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40101 | WSetRvrtTms |  | unimplemented | RW
40103 | WSetRvrtRem |  | unimplemented | R
40105 | VarSetEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40106 | VarSetMod |  | supported | RW
|  | W_MAX_PCT | supported
|  | VAR_MAX_PCT | supported
|  | VAR_AVAIL_PCT | supported
|  | VA_MAX_PCT | supported
|  | VARS | supported
40107 | VarSetPri |  | unimplemented | RW
|  | ACTIVE | unimplemented
|  | REACTIVE | unimplemented
|  | VENDOR | unimplemented
40108 | VarSet |  | supported | RW | 0 | 7200
40110 | VarSetRvrt |  | unimplemented | RW
40112 | VarSetPct |  | supported | RW | -100 | 100
40113 | VarSetPctRvrt |  | unimplemented | RW
40114 | VarSetEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40115 | VarSetRvrtTms |  | unimplemented | RW
40117 | VarSetRvrtRem |  | unimplemented | R
40119 | WRmp |  | unimplemented | RW
40120 | WRmpRef |  | unimplemented | RW
|  | A_MAX | unimplemented
|  | W_MAX | unimplemented
40121 | VarRmp |  | unimplemented | RW
40122 | AntiIslEna |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40123 | PF_SF |  | -3 | R
40124 | WMaxLimPct_SF |  | unimplemented | R
40125 | WSet_SF |  | 0 | R
40126 | WSetPct_SF |  | -2 | R
40127 | VarSet_SF |  | 0 | R
40128 | VarSetPct_SF |  | -2 | R
40129 | PFWInj.PF |  | supported | RW | 0.85 | 1
40130 | PFWInj.Ext |  | supported | RW
|  | OVER_EXCITED | supported
|  | UNDER_EXCITED | supported
40131 | PFWInjRvrt.PF |  | unimplemented | RW
40132 | PFWInjRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented
40133 | PFWAbs.PF |  | unimplemented | RW
40134 | PFWAbs.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented
40135 | PFWAbsRvrt.PF |  | unimplemented | RW
40136 | PFWAbsRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented

## 715
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40137 | ID |  | 715 | R
40138 | L |  | 7 | R
40139 | LocRemCtl |  | unimplemented | R
|  | REMOTE | unimplemented
|  | LOCAL | unimplemented
40140 | DERHb |  | unimplemented | R
40142 | ControllerHb |  | unimplemented | RW
40144 | AlarmReset |  | unimplemented | RW
40145 | OpCtl |  | supported | RW
|  | STOP | supported
|  | START | supported
|  | ENTER_STANDBY | supported
|  | EXIT_STANDBY | supported