## Instructions
SunSpec PICS
This SunSpec PICS was generated by SunSpec Dashboard v3.8.2 based on the model contents of the connected device.
Most of the necessary information is populated but the PICS must be completed before submission by performing the following steps:
1. Examine the entry in the 'Value' column for each point to verify correctness:
- Common model (1) points that are implemented should contain the current value.
- All other model points that are implemented and have a variable value should contain the string 'supported'.
- All other model points that are implemented and have a constant value should contain the constant value.
It is assumed that scale factors are constants. If they are not, change the value to 'supported'.
- All unimplemented points should contain the string 'unimplemented'.
- For each enumeration or bit field entry that is not implemented, change the string to 'unimplemented'.
2. Examine the 'R/W' column to ensure the access is correct. It should be either 'R' or 'RW'.
3. Some points require a value range be specified. Points that have a grey background in the Min and Max column must
have a minimum and maximum value specified in the Min and Max columns. The value should be the value with the scale
factor applied. For example, a value specified in these fields would be 97.34 not 9734 if the scale factor is -2.
For models that have repeating elements, the value range is specified on the points in the first element and are
applicable for all of the repeating elements.
4. For any point that has an implementation deviation or special considerations indicate the issue in the 'Conformance Notes' column.
The certificate number will be filled in when certification is complete and this file will be archived with the Testing Info tab removed
along with a copy of the certificate on sunspec.org.

## Product and Testing Info
Product Information
Product Type | Inverter
Manufacturer Name | SINEXCEL
Product Name | Converter(Energy Storage Inverter)
Product Model Numbers | PWS1-135M-EX,PWS1-135M-EX-R, PWS1-125M-EX,PWS1-125M-EX-R, PWS1-160M-H-EX,PWS1-125M-H-EX, PWX1-1575KTL-H-EX,PWX1-1250KTL-H-EX, PWS1-1725KTL-H-EX-8M1,PWS1-1725KTL-H-EX-8M1-O, PWS1-1725KTL-H-EX-7M1,PWS1-1725KTL-H-EX-7M1-O, PWS1-1725KTL-H-EX-6M1,PWS1-1725KTL-H-EX-6M1-O, PWS1-1725KTL-H-EX-5M1,PWS1-1725KTL-H-EX-5M1-O, PWS1-1725KTL-H-EX-4M1,PWS1-1725KTL-H-EX-4M1-O, PWS1-1725KTL-H-EX-3M1,PWS1-1725KTL-H-EX-3M1-O, PWS1-1725KTL-H-EX-2M1,PWS1-1725KTL-H-EX-2M1-O, PWS1-1725KTL-H-EX-1M1,PWS1-1725KTL-H-EX-1M1-O, PWS1-1725KTL-HEX-8M2,PWS1-1725KTL-HEX--8M2-O, PWS1-1725KTL-HEX-6M2,PWS1-1725KTL-HEX--6M2-O, PWS1-1725KTL-HEX-4M2,PWS1-1725KTL-HEX--4M2-O, PWS1-1725KTL-HEX-2M2,PWS1-1725KTL-HEX--2M2-O, PWS1-1725KTL-HEX-8M4,PWS1-1725KTL-HEX-8M4-O, PWS1-1725KTL-HEX-6M4,PWS1-1725KTL-HEX-6M4-O, PWS1-1725KTL-HEX-4M4,PWS1-1725KTL-HEX-4M4-O, PWS1-1725KTL-HEX-2M4,PWS1-1725KTL-HEX-2M4-O, PWS1-1725KTL-HEX-8M8,PWS1-1725KTL-HEX-8M8-O, PWS1-1725KTL-HEX-7M8,PWS1-1725KTL-HEX-7M8-O, PWS1-1725KTL-HEX-6M8,PWS1-1725KTL-HEX-6M8-O, PWS1-1725KTL-HEX-5M8,PWS1-1725KTL-HEX-5M8-O, PWS1-1725KTL-HEX-4M8,PWS1-1725KTL-HEX-4M8-O, PWS1-1725KTL-HEX-3M8,PWS1-1725KTL-HEX-3M8-O, PWS1-1725KTL-HEX-2M8,PWS1-1725KTL-HEX-2M8-O, PWS1-1725KTL-HEX-1M8,PWS1-1725KTL-HEX-1M8-O, PWS1-500KTL-EX-1M1, PWS1-500KTL-EX-2M1, PWS1-500KTL-EX-3M1, PWS1-500KTL-EX-4M1, PWS1-500KTL-EX-5M1, PWS1-500KTL-EX-6M1, PWS1-500KTL-EX-7M1, PWS1-500KTL-EX-8M1, PWS1-500KTL-EX-2M4, PWS1-500KTL-EX-4M4, PWS1-500KTL-EX-6M4, PWS1-500KTL-EX-8M4, PWS1-500KTL-EX-1M8, PWS1-500KTL-EX-2M8, PWS1-500KTL-EX-3M8, PWS1-500KTL-EX-4M8, PWS1-500KTL-EX-5M8, PWS1-500KTL-EX-6M8, PWS1-500KTL-EX-7M8, PWS1-500KTL-EX-8M8, PWS2-30P-EX，PWS2-29P-EX
Submitter Information
Full Name | qiujie_zhang
Job Title | Certification Engineer
Company Name | Shenzhen Sinexcel Electric Co.,Ltd.
Relationship to Manufacturer | Employee
Email | qiujie_zhang@sinexcel.com
Phone | 86-0755-86511588
Device Under Test Information
Test Type | SunSpec Modbus Conformance Certification
Firmware Version Tested | V1227
Firmware Checksum (in hex) | fe4434baec1e89281b985d3bf5abc3db
Interface Type | RTU
If RTU
Interface Name | COM12
Unit ID | 1
Baud Rate | 19200
Parity | None
Timeout (secs) | 5
If Modbus TCP
IP Address
IP Port
Unit ID
If IEEE 2030.5
IP Address
IP Port
Poll Rate
Client PIN
Timeout (secs)
Reserved For SunSpec Alliance
SunSpec Certificate Number | SM-000053
Certificate Signer Name | Erin Mahan
Certificate Issued Date | 2026-05-29
Certificate Archive Location | https://sunspec.org/wp-content/uploads/2009/03/Sinexcel_Modbus_Certificate_SM000053.pdf

## Test Lab Settings
Target Definition | Target Definition Label | Param | Param Label | Param Value

## IEEE 1547 Electrical Test Setup
Test Category | Param Definition | Param Definition Label | Param | Param Label | Param Unit | Param Value

## 1
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50002 | ID |  | 1 | R | 1 | 1
50003 | L |  | 66 | R
50004 | Mn |  | SINEXCEL | R
50020 | Md |  | PWX1-1575KTL-H-EX | R
50036 | Opt |  | unimplemented | R
50044 | Vr |  | V1227 | R
50052 | SN |  | PCS-SYSTEM-INIT | R
50068 | DA |  | supported | RW | 1 | 247
50069 | Pad |  | 32768 | R

## 701
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50070 | ID |  | 701 | R | 701 | 701
50071 | L |  | 153 | R
50072 | ACType |  | supported | R
|  | SINGLE_PHASE | supported
|  | SPLIT_PHASE | supported
|  | THREE_PHASE | supported
50073 | St |  | supported | R
|  | OFF | supported
|  | ON | supported
50074 | InvSt |  | supported | R
|  | OFF | supported
|  | SLEEPING | supported
|  | STARTING | supported
|  | RUNNING | supported
|  | THROTTLED | supported
|  | SHUTTING_DOWN | supported
|  | FAULT | supported
|  | STANDBY | supported
50075 | ConnSt |  | supported | R
|  | DISCONNECTED | supported
|  | CONNECTED | supported
50076 | Alrm |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | DC_OVER_VOLT | unimplemented
|  | AC_DISCONNECT | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | GRID_DISCONNECT | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | OVER_FREQUENCY | unimplemented
|  | UNDER_FREQUENCY | unimplemented
|  | AC_OVER_VOLT | unimplemented
|  | AC_UNDER_VOLT | unimplemented
|  | BLOWN_STRING_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | HW_TEST_FAILURE | unimplemented
|  | MANUFACTURER_ALRM | unimplemented
50078 | DERMode |  | unimplemented | R
|  | GRID_FOLLOWING | unimplemented
|  | GRID_FORMING | unimplemented
|  | PV_CLIPPED | unimplemented
50080 | W |  | supported | R
50081 | VA |  | supported | R
50082 | Var |  | supported | R
50083 | PF |  | supported | R
50084 | A |  | supported | R
50085 | LLV |  | unimplemented | R
50086 | LNV |  | unimplemented | R
50087 | Hz |  | supported | R
50089 | TotWhInj |  | supported | R
50093 | TotWhAbs |  | supported | R
50097 | TotVarhInj |  | unimplemented | R
50101 | TotVarhAbs |  | unimplemented | R
50105 | TmpAmb |  | supported | R
50106 | TmpCab |  | unimplemented | R
50107 | TmpSnk |  | unimplemented | R
50108 | TmpTrns |  | unimplemented | R
50109 | TmpSw |  | unimplemented | R
50110 | TmpOt |  | unimplemented | R
50111 | WL1 |  | supported | R
50112 | VAL1 |  | supported | R
50113 | VarL1 |  | supported | R
50114 | PFL1 |  | supported | R
50115 | AL1 |  | supported | R
50116 | VL1L2 |  | supported | R
50117 | VL1 |  | supported | R
50118 | TotWhInjL1 |  | supported | R
50122 | TotWhAbsL1 |  | supported | R
50126 | TotVarhInjL1 |  | supported | R
50130 | TotVarhAbsL1 |  | supported | R
50134 | WL2 |  | supported | R
50135 | VAL2 |  | supported | R
50136 | VarL2 |  | supported | R
50137 | PFL2 |  | supported | R
50138 | AL2 |  | supported | R
50139 | VL2L3 |  | supported | R
50140 | VL2 |  | supported | R
50141 | TotWhInjL2 |  | unimplemented | R
50145 | TotWhAbsL2 |  | unimplemented | R
50149 | TotVarhInjL2 |  | unimplemented | R
50153 | TotVarhAbsL2 |  | unimplemented | R
50157 | WL3 |  | supported | R
50158 | VAL3 |  | supported | R
50159 | VarL3 |  | supported | R
50160 | PFL3 |  | supported | R
50161 | AL3 |  | supported | R
50162 | VL3L1 |  | supported | R
50163 | VL3 |  | supported | R
50164 | TotWhInjL3 |  | unimplemented | R
50168 | TotWhAbsL3 |  | unimplemented | R
50172 | TotVarhInjL3 |  | unimplemented | R
50176 | TotVarhAbsL3 |  | unimplemented | R
50180 | ThrotPct |  | unimplemented | R
50181 | ThrotSrc |  | supported | R
|  | MAX_W | supported
|  | FIXED_W | supported
|  | FIXED_VAR | supported
|  | FIXED_PF | supported
|  | VOLT_VAR | supported
|  | FREQ_WATT | supported
|  | DYN_REACT_CURR | supported
|  | LVRT | supported
|  | HVRT | supported
|  | WATT_VAR | supported
|  | VOLT_WATT | supported
|  | SCHEDULED | supported
|  | LFRT | supported
|  | HFRT | supported
|  | DERATED | supported
50183 | A_SF |  | -1 | R
50184 | V_SF |  | -1 | R
50185 | Hz_SF |  | -2 | R
50186 | W_SF |  | 2 | R
50187 | PF_SF |  | -2 | R
50188 | VA_SF |  | 2 | R
50189 | Var_SF |  | 2 | R
50190 | TotWh_SF |  | unimplemented | R
50191 | TotVarh_SF |  | unimplemented | R
50192 | Tmp_SF |  | 1 | R
50193 | MnAlrmInfo |  | unimplemented | R

## 702
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50225 | ID |  | 702 | R | 702 | 702
50226 | L |  | 50 | R
50227 | WMaxRtg |  | unimplemented | R
50228 | WOvrExtRtg |  | unimplemented | R
50229 | WOvrExtRtgPF |  | unimplemented | R
50230 | WUndExtRtg |  | unimplemented | R
50231 | WUndExtRtgPF |  | unimplemented | R
50232 | VAMaxRtg |  | unimplemented | R
50233 | VarMaxInjRtg |  | unimplemented | R
50234 | VarMaxAbsRtg |  | unimplemented | R
50235 | WChaRteMaxRtg |  | unimplemented | R
50236 | WDisChaRteMaxRtg |  | unimplemented | R
50237 | VAChaRteMaxRtg |  | unimplemented | R
50238 | VADisChaRteMaxRtg |  | unimplemented | R
50239 | VNomRtg |  | unimplemented | R
50240 | VMaxRtg |  | unimplemented | R
50241 | VMinRtg |  | unimplemented | R
50242 | AMaxRtg |  | unimplemented | R
50243 | PFOvrExtRtg |  | unimplemented | R
50244 | PFUndExtRtg |  | unimplemented | R
50245 | ReactSusceptRtg |  | unimplemented | R
50246 | NorOpCatRtg |  | unimplemented | R
|  | CAT_A | unimplemented
|  | CAT_B | unimplemented
50247 | AbnOpCatRtg |  | unimplemented | R
|  | CAT_1 | unimplemented
|  | CAT_2 | unimplemented
|  | CAT_3 | unimplemented
50248 | CtrlModes |  | unimplemented | R
|  | MAX_W | unimplemented
|  | FIXED_W | unimplemented
|  | FIXED_VAR | unimplemented
|  | FIXED_PF | unimplemented
|  | VOLT_VAR | unimplemented
|  | FREQ_WATT | unimplemented
|  | DYN_REACT_CURR | unimplemented
|  | LV_TRIP | unimplemented
|  | HV_TRIP | unimplemented
|  | WATT_VAR | unimplemented
|  | VOLT_WATT | unimplemented
|  | SCHEDULED | unimplemented
|  | LF_TRIP | unimplemented
|  | HF_TRIP | unimplemented
50250 | IntIslandCatRtg |  | unimplemented | R
|  | UNCATEGORIZED | unimplemented
|  | INT_ISL_CAPABLE | unimplemented
|  | BLACK_START_CAPABLE | unimplemented
|  | ISOCH_CAPABLE | unimplemented
50251 | WMax |  | unimplemented | RW
50252 | WMaxOvrExt |  | unimplemented | RW
50253 | WOvrExtPF |  | unimplemented | RW
50254 | WMaxUndExt |  | unimplemented | RW
50255 | WUndExtPF |  | unimplemented | RW
50256 | VAMax |  | unimplemented | RW
50257 | VarMaxInj |  | unimplemented | RW
50258 | VarMaxAbs |  | unimplemented | RW
50259 | WChaRteMax |  | unimplemented | RW
50260 | WDisChaRteMax |  | unimplemented | RW
50261 | VAChaRteMax |  | unimplemented | RW
50262 | VADisChaRteMax |  | unimplemented | RW
50263 | VNom |  | unimplemented | RW
50264 | VMax |  | unimplemented | RW
50265 | VMin |  | unimplemented | RW
50266 | AMax |  | unimplemented | RW
50267 | PFOvrExt |  | unimplemented | RW
50268 | PFUndExt |  | unimplemented | RW
50269 | IntIslandCat |  | unimplemented | RW
|  | UNCATEGORIZED | unimplemented
|  | INT_ISL_CAPABLE | unimplemented
|  | BLACK_START_CAPABLE | unimplemented
|  | ISOCH_CAPABLE | unimplemented
50270 | W_SF |  | unimplemented | R
50271 | PF_SF |  | -2 | R
50272 | VA_SF |  | unimplemented | R
50273 | Var_SF |  | unimplemented | R
50274 | V_SF |  | unimplemented | R
50275 | A_SF |  | unimplemented | R
50276 | S_SF |  | unimplemented | R

## 703
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50277 | ID |  | 703 | R | 703 | 703
50278 | L |  | 17 | R
50279 | ES |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50280 | ESVHi |  | supported | RW | 100 | 135
50281 | ESVLo |  | supported | RW | 20 | 100
50282 | ESHzHi |  | supported | RW | 50.01 | 56
50284 | ESHzLo |  | supported | RW | 40 | 49.99
50286 | ESDlyTms |  | supported | RW | 0 | 1800
50288 | ESRndTms |  | supported | RW | 1 | 1
50290 | ESRmpTms |  | unimplemented | RW
50292 | ESDlyRemTms |  | unimplemented | R
50294 | V_SF |  | -1 | R
50295 | Hz_SF |  | -2 | R

## 704
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50296 | ID |  | 704 | R | 704 | 704
50297 | L |  | 65 | R
50298 | PFWInjEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50299 | PFWInjEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50300 | PFWInjRvrtTms |  | unimplemented | RW
50302 | PFWInjRvrtRem |  | unimplemented | R
50304 | PFWAbsEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50305 | PFWAbsEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50306 | PFWAbsRvrtTms |  | unimplemented | RW
50308 | PFWAbsRvrtRem |  | unimplemented | R
50310 | WMaxLimPctEna |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50311 | WMaxLimPct |  | unimplemented | RW
50312 | WMaxLimPctRvrt |  | unimplemented | RW
50313 | WMaxLimPctEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50314 | WMaxLimPctRvrtTms |  | unimplemented | RW
50316 | WMaxLimPctRvrtRem |  | unimplemented | R
50318 | WSetEna |  | supported | RW
|  | DISABLED | unimplemented
|  | ENABLED | supported
50319 | WSetMod |  | supported | RW
|  | W_MAX_PCT | supported
|  | WATTS | supported
50320 | WSet |  | supported | RW | -1575000 | 1575000
50322 | WSetRvrt |  | unimplemented | RW
50324 | WSetPct |  | supported | RW | -100 | 100
50325 | WSetPctRvrt |  | unimplemented | RW
50326 | WSetEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50327 | WSetRvrtTms |  | unimplemented | RW
50329 | WSetRvrtRem |  | unimplemented | R
50331 | VarSetEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50332 | VarSetMod |  | supported | RW
|  | W_MAX_PCT | supported
|  | VAR_MAX_PCT | unimplemented
|  | VAR_AVAIL_PCT | unimplemented
|  | VA_MAX_PCT | unimplemented
|  | VARS | supported
50333 | VarSetPri |  | supported | RW
|  | ACTIVE | unimplemented
|  | REACTIVE | supported
|  | VENDOR | unimplemented
50334 | VarSet |  | supported | RW | -1575000 | 1575000
50336 | VarSetRvrt |  | unimplemented | RW
50338 | VarSetPct |  | supported | RW | -100 | 100
50339 | VarSetPctRvrt |  | unimplemented | RW
50340 | VarSetEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50341 | VarSetRvrtTms |  | unimplemented | RW
50343 | VarSetRvrtRem |  | unimplemented | R
50345 | WRmp |  | supported | RW | 1 | 300
50346 | WRmpRef |  | supported | RW
|  | A_MAX | unimplemented
|  | W_MAX | supported
50347 | VarRmp |  | supported | RW | 1 | 300
50348 | AntiIslEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50349 | PF_SF |  | -2 | R
50350 | WMaxLimPct_SF |  | unimplemented | R
50351 | WSet_SF |  | 2 | R
50352 | WSetPct_SF |  | 0 | R
50353 | VarSet_SF |  | 2 | R
50354 | VarSetPct_SF |  | 0 | R
50355 | PFWInj.PF |  | supported | RW | 0.9 | 1
50356 | PFWInj.Ext |  | supported | RW
|  | OVER_EXCITED | supported
|  | UNDER_EXCITED | supported
50357 | PFWInjRvrt.PF |  | unimplemented | RW
50358 | PFWInjRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented
50359 | PFWAbs.PF |  | supported | RW | 0.9 | 1
50360 | PFWAbs.Ext |  | supported | RW
|  | OVER_EXCITED | supported
|  | UNDER_EXCITED | supported
50361 | PFWAbsRvrt.PF |  | unimplemented | RW
50362 | PFWAbsRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented

## 714
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50363 | ID |  | 714 | R | 714 | 714
50364 | L |  | 43 | R
50365 | PrtAlrms |  | supported | R
50367 | NPrt |  | 1 | R
50368 | DCA |  | supported | R
50369 | DCW |  | supported | R
50370 | DCWhInj |  | unimplemented | R
50374 | DCWhAbs |  | unimplemented | R
50378 | DCA_SF |  | -1 | R
50379 | DCV_SF |  | -1 | R
50380 | DCW_SF |  | 2 | R
50381 | DCWH_SF |  | unimplemented | R
50382 | Tmp_SF |  | unimplemented | R
50383 | Prt.1.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
50384 | Prt.1.ID |  | supported | R
50385 | Prt.1.IDStr |  | unimplemented | R
50393 | Prt.1.DCA |  | supported | R
50394 | Prt.1.DCV |  | supported | R
50395 | Prt.1.DCW |  | supported | R
50396 | Prt.1.DCWhInj |  | unimplemented | R
50400 | Prt.1.DCWhAbs |  | unimplemented | R
50404 | Prt.1.Tmp |  | unimplemented | R
50405 | Prt.1.DCSta |  | supported | R
|  | OFF | supported
|  | ON | supported
|  | WARNING | supported
|  | ERROR | supported
50406 | Prt.1.DCAlrm |  | supported | R
|  | GROUND_FAULT | supported
|  | INPUT_OVER_VOLTAGE | supported
|  | DC_DISCONNECT | supported
|  | CABINET_OPEN | supported
|  | MANUAL_SHUTDOWN | supported
|  | OVER_TEMP | supported
|  | BLOWN_FUSE | supported
|  | UNDER_TEMP | supported
|  | MEMORY_LOSS | supported
|  | ARC_DETECTION | supported
|  | RESERVED | supported
|  | TEST_FAILED | supported
|  | INPUT_UNDER_VOLTAGE | supported
|  | INPUT_OVER_CURRENT | supported