## Instructions
SunSpec PICS
This SunSpec PICS was generated by SunSpec Dashboard v3.8.2 based on the model contents of the connected device.
Most of the necessary information is populated but the PICS must be completed before submission by performing the following steps:
1. Examine the entry in the 'Value' column for each point to verify correctness:
- Common model (1) points that are implemented should contain the current value.
- All other model points that are implemented and have a variable value should contain the string 'supported'.
- All other model points that are implemented and have a constant value should contain the constant value.
It is assumed that scale factors are constants. If they are not, change the value to 'supported'.
- All unimplemented points should contain the string 'unimplemented'.
- For each enumeration or bit field entry that is not implemented, change the string to 'unimplemented'.
2. Examine the 'R/W' column to ensure the access is correct. It should be either 'R' or 'RW'.
3. Some points require a value range be specified. Points that have a grey background in the Min and Max column must
have a minimum and maximum value specified in the Min and Max columns. The value should be the value with the scale
factor applied. For example, a value specified in these fields would be 97.34 not 9734 if the scale factor is -2.
For models that have repeating elements, the value range is specified on the points in the first element and are
applicable for all of the repeating elements.
4. For any point that has an implementation deviation or special considerations indicate the issue in the 'Conformance Notes' column.
The certificate number will be filled in when certification is complete and this file will be archived with the Testing Info tab removed
along with a copy of the certificate on sunspec.org.

## Product and Testing Info
Product Information
Product Type | Inverter
Manufacturer Name | AISWEI Technology Co.,Ltd
Product Name | Grid-connected PV inverter
Product Model Numbers | ASW25K-LT-G3,ASW27K-LT-G3,ASW30K-LT-G3,ASW33K-LT-G3,ASW36K-LT-G3,ASW40K-LT-G3; ASW45K-LT-G3,ASW50K-LT-G3,ASW60K-LT-G3; ASW75K-LT,ASW80K-LT,ASW100K-LT,ASW110K-LT,ASW125K-LT,ASW150K-LT; ASW250K-HT,ASW300K-HT,ASW333K-HT,ASW350K-HT,ASW360K-HT;
Submitter Information
Full Name | Sandy Gong
Job Title | Safety Dept. Manager
Company Name | AISWEI Technology Co.,Ltd
Relationship to Manufacturer | Employee
Email | sandy.gong@aiswei-tech.com
Phone | +86 18662276245
Device Under Test Information
Test Type | SunSpec Modbus Conformance Certification
Firmware Version Tested | V610
Firmware Checksum (in hex) | A3D35EBA2516E70D8268701BE13E9E5E
Interface Type | RTU
If RTU
Interface Name | COM5
Unit ID | 3
Baud Rate | 9600
Parity | None
Timeout (secs)
If Modbus TCP
IP Address
IP Port
Unit ID
If IEEE 2030.5
IP Address
IP Port
Poll Rate
Client PIN
Timeout (secs)
Reserved For SunSpec Alliance
SunSpec Certificate Number | SM-000058
Certificate Signer Name | Dylan Tansy
Certificate Issued Date | Wednesday, July 10, 2026
Certificate Archive Location | https://sunspec.org/wp-content/uploads/2009/03/Updated-Models_AISWEI_Modbus_Certificate_SM000058.pdf

## Test Lab Settings
Target Definition | Target Definition Label | Param | Param Label | Param Value

## IEEE 1547 Electrical Test Setup
Test Category | Param Definition | Param Definition Label | Param | Param Label | Param Unit | Param Value

## 1
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40002 | ID |  | 1 | R | 1 | 1
40003 | L |  | 66 | R
40004 | Mn |  | AISWEI | R
40020 | Md |  | ASW 40K-LT-G3 | R
40036 | Opt |  | unimplemented | R
40044 | Vr |  | V610-03041-25 | R
40052 | SN |  | TA004060H2620004 | R
40068 | DA |  | supported | RW | 1 | 247
40069 | Pad |  | 32768 | R

## 103
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40070 | ID |  | 103 | R
40071 | L |  | 50 | R
40072 | A |  | supported | R
40073 | AphA |  | supported | R
40074 | AphB |  | supported | R
40075 | AphC |  | supported | R
40076 | A_SF |  | supported | R
40077 | PPVphAB |  | supported | R
40078 | PPVphBC |  | supported | R
40079 | PPVphCA |  | supported | R
40080 | PhVphA |  | supported | R
40081 | PhVphB |  | supported | R
40082 | PhVphC |  | supported | R
40083 | V_SF |  | supported | R
40084 | W |  | supported | R
40085 | W_SF |  | supported | R
40086 | Hz |  | supported | R
40087 | Hz_SF |  | supported | R
40088 | VA |  | supported | R
40089 | VA_SF |  | supported | R
40090 | VAr |  | supported | R
40091 | VAr_SF |  | supported | R
40092 | PF |  | supported | R
40093 | PF_SF |  | supported | R
40094 | WH |  | supported | R
40096 | WH_SF |  | supported | R
40097 | DCA |  | unimplemented | R
40098 | DCA_SF |  | unimplemented | R
40099 | DCV |  | unimplemented | R
40100 | DCV_SF |  | unimplemented | R
40101 | DCW |  | unimplemented | R
40102 | DCW_SF |  | unimplemented | R
40103 | TmpCab |  | supported | R
40104 | TmpSnk |  | unimplemented | R
40105 | TmpTrns |  | unimplemented | R
40106 | TmpOt |  | unimplemented | R
40107 | Tmp_SF |  | supported | R
40108 | St |  | supported | R
|  | OFF | supported
|  | SLEEPING | supported
|  | STARTING | supported
|  | MPPT | supported
|  | THROTTLED | supported
|  | SHUTTING_DOWN | supported
|  | FAULT | supported
|  | STANDBY | supported
40109 | StVnd |  | unimplemented | R
40110 | Evt1 |  | supported | R
|  | GROUND_FAULT | supported
|  | DC_OVER_VOLT | supported
|  | AC_DISCONNECT | supported
|  | DC_DISCONNECT | supported
|  | GRID_DISCONNECT | supported
|  | CABINET_OPEN | supported
|  | MANUAL_SHUTDOWN | supported
|  | OVER_TEMP | supported
|  | OVER_FREQUENCY | supported
|  | UNDER_FREQUENCY | supported
|  | AC_OVER_VOLT | supported
|  | AC_UNDER_VOLT | supported
|  | BLOWN_STRING_FUSE | supported
|  | UNDER_TEMP | supported
|  | MEMORY_LOSS | supported
|  | HW_TEST_FAILURE | supported
40112 | Evt2 |  | supported | R
40114 | EvtVnd1 |  | unimplemented | R
40116 | EvtVnd2 |  | unimplemented | R
40118 | EvtVnd3 |  | unimplemented | R
40120 | EvtVnd4 |  | unimplemented | R

## 120
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40122 | ID |  | 120 | R
40123 | L |  | 26 | R
40124 | DERTyp |  | supported | R
|  | PV | supported
|  | PV_STOR | supported
40125 | WRtg |  | supported | R
40126 | WRtg_SF |  | supported | R
40127 | VARtg |  | supported | R
40128 | VARtg_SF |  | supported | R
40129 | VArRtgQ1 |  | supported | R
40130 | VArRtgQ2 |  | supported | R
40131 | VArRtgQ3 |  | supported | R
40132 | VArRtgQ4 |  | supported | R
40133 | VArRtg_SF |  | supported | R
40134 | ARtg |  | supported | R
40135 | ARtg_SF |  | supported | R
40136 | PFRtgQ1 |  | supported | R
40137 | PFRtgQ2 |  | supported | R
40138 | PFRtgQ3 |  | supported | R
40139 | PFRtgQ4 |  | supported | R
40140 | PFRtg_SF |  | supported | R
40141 | WHRtg |  | unimplemented | R
40142 | WHRtg_SF |  | unimplemented | R
40143 | AhrRtg |  | unimplemented | R
40144 | AhrRtg_SF |  | unimplemented | R
40145 | MaxChaRte |  | unimplemented | R
40146 | MaxChaRte_SF |  | unimplemented | R
40147 | MaxDisChaRte |  | unimplemented | R
40148 | MaxDisChaRte_SF |  | unimplemented | R
40149 | Pad |  | supported | R

## 121
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40150 | ID |  | 121 | R
40151 | L |  | 30 | R
40152 | WMax |  | supported | RW | 0 | 40000
40153 | VRef |  | supported | RW | 220 | 240
40154 | VRefOfs |  | supported | RW | 0 | 20
40155 | VMax |  | unimplemented | RW
40156 | VMin |  | unimplemented | RW
40157 | VAMax |  | unimplemented | RW
40158 | VArMaxQ1 |  | unimplemented | RW
40159 | VArMaxQ2 |  | unimplemented | RW
40160 | VArMaxQ3 |  | unimplemented | RW
40161 | VArMaxQ4 |  | unimplemented | RW
40162 | WGra |  | unimplemented | RW
40163 | PFMinQ1 |  | unimplemented | RW
40164 | PFMinQ2 |  | unimplemented | RW
40165 | PFMinQ3 |  | unimplemented | RW
40166 | PFMinQ4 |  | unimplemented | RW
40167 | VArAct |  | unimplemented | RW
|  | SWITCH | unimplemented
|  | MAINTAIN | unimplemented
40168 | ClcTotVA |  | unimplemented | RW
|  | VECTOR | unimplemented
|  | ARITHMETIC | unimplemented
40169 | MaxRmpRte |  | unimplemented | RW
40170 | ECPNomHz |  | unimplemented | RW
40171 | ConnPh |  | unimplemented | RW
|  | A | unimplemented
|  | B | unimplemented
|  | C | unimplemented
40172 | WMax_SF |  | supported | R
40173 | VRef_SF |  | supported | R
40174 | VRefOfs_SF |  | supported | R
40175 | VMinMax_SF |  | supported | R
40176 | VAMax_SF |  | supported | R
40177 | VArMax_SF |  | unimplemented | R
40178 | WGra_SF |  | unimplemented | R
40179 | PFMin_SF |  | unimplemented | R
40180 | MaxRmpRte_SF |  | unimplemented | R
40181 | ECPNomHz_SF |  | unimplemented | R

## 123
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40182 | ID |  | 123 | R
40183 | L |  | 24 | R
40184 | Conn_WinTms |  | unimplemented | RW
40185 | Conn_RvrtTms |  | unimplemented | RW
40186 | Conn |  | supported | RW
|  | DISCONNECT | supported
|  | CONNECT | supported
40187 | WMaxLimPct |  | supported | RW | 0 | 100
40188 | WMaxLimPct_WinTms |  | unimplemented | RW
40189 | WMaxLimPct_RvrtTms |  | supported | RW | 0 | 60000
40190 | WMaxLimPct_RmpTms |  | supported | RW | 0 | 600
40191 | WMaxLim_Ena |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40192 | OutPFSet |  | supported | RW | 0.8 | 1
40193 | OutPFSet_WinTms |  | unimplemented | RW
40194 | OutPFSet_RvrtTms |  | supported | RW | 0 | 60000
40195 | OutPFSet_RmpTms |  | supported | RW | 0 | 600
40196 | OutPFSet_Ena |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40197 | VArWMaxPct |  | supported | RW | -60 | 60
40198 | VArMaxPct |  | unimplemented | RW
40199 | VArAvalPct |  | unimplemented | RW
40200 | VArPct_WinTms |  | unimplemented | RW
40201 | VArPct_RvrtTms |  | supported | RW | 0 | 60000
40202 | VArPct_RmpTms |  | supported | RW | 0 | 600
40203 | VArPct_Mod |  | supported | RW
|  | NONE | unimplemented
|  | WMax | supported
|  | VArMax | unimplemented
|  | VArAval | unimplemented
40204 | VArPct_Ena |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40205 | WMaxLimPct_SF |  | supported | R
40206 | OutPFSet_SF |  | supported | R
40207 | VArPct_SF |  | supported | R

## 160
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40208 | ID |  | 160 | R
40209 | L |  | 68 | R
40210 | DCA_SF |  | supported | R
40211 | DCV_SF |  | supported | R
40212 | DCW_SF |  | supported | R
40213 | DCWH_SF |  | unimplemented | R
40214 | Evt |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | INPUT_OVER_VOLTAGE | unimplemented
|  | RESERVED_2 | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | RESERVED_4 | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | RESERVED_8 | unimplemented
|  | RESERVED_9 | unimplemented
|  | RESERVED_10 | unimplemented
|  | RESERVED_11 | unimplemented
|  | BLOWN_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | ARC_DETECTION | unimplemented
|  | RESERVED_16 | unimplemented
|  | RESERVED_17 | unimplemented
|  | RESERVED_18 | unimplemented
|  | RESERVED_19 | unimplemented
|  | TEST_FAILED | unimplemented
|  | INPUT_UNDER_VOLTAGE | unimplemented
|  | INPUT_OVER_CURRENT | unimplemented
40216 | N |  | supported | R
40217 | TmsPer |  | unimplemented | R
40218 | module.1.ID |  | supported | R
40219 | module.1.IDStr |  | unimplemented | R
40227 | module.1.DCA |  | supported | R
40228 | module.1.DCV |  | supported | R
40229 | module.1.DCW |  | supported | R
40230 | module.1.DCWH |  | unimplemented | R
40232 | module.1.Tms |  | unimplemented | R
40234 | module.1.Tmp |  | unimplemented | R
40235 | module.1.DCSt |  | unimplemented | R
|  | OFF | unimplemented
|  | SLEEPING | unimplemented
|  | STARTING | unimplemented
|  | MPPT | unimplemented
|  | THROTTLED | unimplemented
|  | SHUTTING_DOWN | unimplemented
|  | FAULT | unimplemented
|  | STANDBY | unimplemented
|  | TEST | unimplemented
|  | RESERVED_10 | unimplemented
40236 | module.1.DCEvt |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | INPUT_OVER_VOLTAGE | unimplemented
|  | RESERVED_2 | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | RESERVED_4 | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | RESERVED_8 | unimplemented
|  | RESERVED_9 | unimplemented
|  | RESERVED_10 | unimplemented
|  | RESERVED_11 | unimplemented
|  | BLOWN_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | ARC_DETECTION | unimplemented
|  | RESERVED_16 | unimplemented
|  | RESERVED_17 | unimplemented
|  | RESERVED_18 | unimplemented
|  | RESERVED_19 | unimplemented
|  | TEST_FAILED | unimplemented
|  | INPUT_UNDER_VOLTAGE | unimplemented
|  | INPUT_OVER_CURRENT | unimplemented
40238 | module.2.ID |  | supported | R
40239 | module.2.IDStr |  | unimplemented | R
40247 | module.2.DCA |  | supported | R
40248 | module.2.DCV |  | supported | R
40249 | module.2.DCW |  | supported | R
40250 | module.2.DCWH |  | unimplemented | R
40252 | module.2.Tms |  | unimplemented | R
40254 | module.2.Tmp |  | unimplemented | R
40255 | module.2.DCSt |  | unimplemented | R
|  | OFF | unimplemented
|  | SLEEPING | unimplemented
|  | STARTING | unimplemented
|  | MPPT | unimplemented
|  | THROTTLED | unimplemented
|  | SHUTTING_DOWN | unimplemented
|  | FAULT | unimplemented
|  | STANDBY | unimplemented
|  | TEST | unimplemented
|  | RESERVED_10 | unimplemented
40256 | module.2.DCEvt |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | INPUT_OVER_VOLTAGE | unimplemented
|  | RESERVED_2 | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | RESERVED_4 | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | RESERVED_8 | unimplemented
|  | RESERVED_9 | unimplemented
|  | RESERVED_10 | unimplemented
|  | RESERVED_11 | unimplemented
|  | BLOWN_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | ARC_DETECTION | unimplemented
|  | RESERVED_16 | unimplemented
|  | RESERVED_17 | unimplemented
|  | RESERVED_18 | unimplemented
|  | RESERVED_19 | unimplemented
|  | TEST_FAILED | unimplemented
|  | INPUT_UNDER_VOLTAGE | unimplemented
|  | INPUT_OVER_CURRENT | unimplemented
40258 | module.3.ID |  | supported | R
40259 | module.3.IDStr |  | unimplemented | R
40267 | module.3.DCA |  | supported | R
40268 | module.3.DCV |  | supported | R
40269 | module.3.DCW |  | supported | R
40270 | module.3.DCWH |  | unimplemented | R
40272 | module.3.Tms |  | unimplemented | R
40274 | module.3.Tmp |  | unimplemented | R
40275 | module.3.DCSt |  | unimplemented | R
|  | OFF | unimplemented
|  | SLEEPING | unimplemented
|  | STARTING | unimplemented
|  | MPPT | unimplemented
|  | THROTTLED | unimplemented
|  | SHUTTING_DOWN | unimplemented
|  | FAULT | unimplemented
|  | STANDBY | unimplemented
|  | TEST | unimplemented
|  | RESERVED_10 | unimplemented
40276 | module.3.DCEvt |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | INPUT_OVER_VOLTAGE | unimplemented
|  | RESERVED_2 | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | RESERVED_4 | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | RESERVED_8 | unimplemented
|  | RESERVED_9 | unimplemented
|  | RESERVED_10 | unimplemented
|  | RESERVED_11 | unimplemented
|  | BLOWN_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | ARC_DETECTION | unimplemented
|  | RESERVED_16 | unimplemented
|  | RESERVED_17 | unimplemented
|  | RESERVED_18 | unimplemented
|  | RESERVED_19 | unimplemented
|  | TEST_FAILED | unimplemented
|  | INPUT_UNDER_VOLTAGE | unimplemented
|  | INPUT_OVER_CURRENT | unimplemented

## 701
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40278 | ID |  | 701 | R | 701 | 701
40279 | L |  | 153 | R
40280 | ACType |  | supported | R
|  | SINGLE_PHASE | supported
|  | SPLIT_PHASE | supported
|  | THREE_PHASE | supported
40281 | St |  | supported | R
|  | OFF | supported
|  | ON | supported
40282 | InvSt |  | supported | R
|  | OFF | supported
|  | SLEEPING | supported
|  | STARTING | supported
|  | RUNNING | supported
|  | THROTTLED | supported
|  | SHUTTING_DOWN | supported
|  | FAULT | supported
|  | STANDBY | supported
40283 | ConnSt |  | supported | R
|  | DISCONNECTED | supported
|  | CONNECTED | supported
40284 | Alrm |  | supported | R
|  | GROUND_FAULT | supported
|  | DC_OVER_VOLT | supported
|  | AC_DISCONNECT | supported
|  | DC_DISCONNECT | supported
|  | GRID_DISCONNECT | supported
|  | CABINET_OPEN | supported
|  | MANUAL_SHUTDOWN | supported
|  | OVER_TEMP | supported
|  | OVER_FREQUENCY | supported
|  | UNDER_FREQUENCY | supported
|  | AC_OVER_VOLT | supported
|  | AC_UNDER_VOLT | supported
|  | BLOWN_STRING_FUSE | supported
|  | UNDER_TEMP | supported
|  | MEMORY_LOSS | supported
|  | HW_TEST_FAILURE | supported
|  | MANUFACTURER_ALRM | supported
40286 | DERMode |  | unimplemented | R
|  | GRID_FOLLOWING | unimplemented
|  | GRID_FORMING | unimplemented
|  | PV_CLIPPED | unimplemented
40288 | W |  | supported | R
40289 | VA |  | supported | R
40290 | Var |  | supported | R
40291 | PF |  | supported | R
40292 | A |  | supported | R
40293 | LLV |  | supported | R
40294 | LNV |  | supported | R
40295 | Hz |  | supported | R
40297 | TotWhInj |  | supported | R
40301 | TotWhAbs |  | unimplemented | R
40305 | TotVarhInj |  | unimplemented | R
40309 | TotVarhAbs |  | unimplemented | R
40313 | TmpAmb |  | unimplemented | R
40314 | TmpCab |  | supported | R
40315 | TmpSnk |  | supported | R
40316 | TmpTrns |  | unimplemented | R
40317 | TmpSw |  | unimplemented | R
40318 | TmpOt |  | unimplemented | R
40319 | WL1 |  | supported | R
40320 | VAL1 |  | supported | R
40321 | VarL1 |  | unimplemented | R
40322 | PFL1 |  | unimplemented | R
40323 | AL1 |  | supported | R
40324 | VL1L2 |  | supported | R
40325 | VL1 |  | supported | R
40326 | TotWhInjL1 |  | unimplemented | R
40330 | TotWhAbsL1 |  | unimplemented | R
40334 | TotVarhInjL1 |  | unimplemented | R
40338 | TotVarhAbsL1 |  | unimplemented | R
40342 | WL2 |  | supported | R
40343 | VAL2 |  | supported | R
40344 | VarL2 |  | unimplemented | R
40345 | PFL2 |  | unimplemented | R
40346 | AL2 |  | supported | R
40347 | VL2L3 |  | supported | R
40348 | VL2 |  | supported | R
40349 | TotWhInjL2 |  | unimplemented | R
40353 | TotWhAbsL2 |  | unimplemented | R
40357 | TotVarhInjL2 |  | unimplemented | R
40361 | TotVarhAbsL2 |  | unimplemented | R
40365 | WL3 |  | supported | R
40366 | VAL3 |  | supported | R
40367 | VarL3 |  | unimplemented | R
40368 | PFL3 |  | unimplemented | R
40369 | AL3 |  | supported | R
40370 | VL3L1 |  | supported | R
40371 | VL3 |  | supported | R
40372 | TotWhInjL3 |  | unimplemented | R
40376 | TotWhAbsL3 |  | unimplemented | R
40380 | TotVarhInjL3 |  | unimplemented | R
40384 | TotVarhAbsL3 |  | unimplemented | R
40388 | ThrotPct |  | unimplemented | R
40389 | ThrotSrc |  | unimplemented | R
|  | MAX_W | unimplemented
|  | FIXED_W | unimplemented
|  | FIXED_VAR | unimplemented
|  | FIXED_PF | unimplemented
|  | VOLT_VAR | unimplemented
|  | FREQ_WATT | unimplemented
|  | DYN_REACT_CURR | unimplemented
|  | LVRT | unimplemented
|  | HVRT | unimplemented
|  | WATT_VAR | unimplemented
|  | VOLT_WATT | unimplemented
|  | SCHEDULED | unimplemented
|  | LFRT | unimplemented
|  | HFRT | unimplemented
|  | DERATED | unimplemented
40391 | A_SF |  | -2 | R
40392 | V_SF |  | -1 | R
40393 | Hz_SF |  | -2 | R
40394 | W_SF |  | 1 | R
40395 | PF_SF |  | -4 | R
40396 | VA_SF |  | 1 | R
40397 | Var_SF |  | 1 | R
40398 | TotWh_SF |  | 1 | R
40399 | TotVarh_SF |  | unimplemented | R
40400 | Tmp_SF |  | -1 | R
40401 | MnAlrmInfo |  | unimplemented | R

## 702
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40433 | ID |  | 702 | R | 702 | 702
40434 | L |  | 50 | R
40435 | WMaxRtg |  | 4000 | R
40436 | WOvrExtRtg |  | unimplemented | R
40437 | WOvrExtRtgPF |  | unimplemented | R
40438 | WUndExtRtg |  | unimplemented | R
40439 | WUndExtRtgPF |  | unimplemented | R
40440 | VAMaxRtg |  | 4000 | R
40441 | VarMaxInjRtg |  | unimplemented | R
40442 | VarMaxAbsRtg |  | unimplemented | R
40443 | WChaRteMaxRtg |  | unimplemented | R
40444 | WDisChaRteMaxRtg |  | unimplemented | R
40445 | VAChaRteMaxRtg |  | unimplemented | R
40446 | VADisChaRteMaxRtg |  | unimplemented | R
40447 | VNomRtg |  | 230 | R
40448 | VMaxRtg |  | unimplemented | R
40449 | VMinRtg |  | unimplemented | R
40450 | AMaxRtg |  | 6419 | R
40451 | PFOvrExtRtg |  | unimplemented | R
40452 | PFUndExtRtg |  | unimplemented | R
40453 | ReactSusceptRtg |  | unimplemented | R
40454 | NorOpCatRtg |  | unimplemented | R
|  | CAT_A | unimplemented
|  | CAT_B | unimplemented
40455 | AbnOpCatRtg |  | unimplemented | R
|  | CAT_1 | unimplemented
|  | CAT_2 | unimplemented
|  | CAT_3 | unimplemented
40456 | CtrlModes |  | unimplemented | R
|  | MAX_W | unimplemented
|  | FIXED_W | unimplemented
|  | FIXED_VAR | unimplemented
|  | FIXED_PF | unimplemented
|  | VOLT_VAR | unimplemented
|  | FREQ_WATT | unimplemented
|  | DYN_REACT_CURR | unimplemented
|  | LV_TRIP | unimplemented
|  | HV_TRIP | unimplemented
|  | WATT_VAR | unimplemented
|  | VOLT_WATT | unimplemented
|  | SCHEDULED | unimplemented
|  | LF_TRIP | unimplemented
|  | HF_TRIP | unimplemented
40458 | IntIslandCatRtg |  | unimplemented | R
|  | UNCATEGORIZED | unimplemented
|  | INT_ISL_CAPABLE | unimplemented
|  | BLACK_START_CAPABLE | unimplemented
|  | ISOCH_CAPABLE | unimplemented
40459 | WMax |  | unimplemented | RW
40460 | WMaxOvrExt |  | unimplemented | RW
40461 | WOvrExtPF |  | unimplemented | RW
40462 | WMaxUndExt |  | unimplemented | RW
40463 | WUndExtPF |  | unimplemented | RW
40464 | VAMax |  | unimplemented | RW
40465 | VarMaxInj |  | unimplemented | RW
40466 | VarMaxAbs |  | unimplemented | RW
40467 | WChaRteMax |  | unimplemented | RW
40468 | WDisChaRteMax |  | unimplemented | RW
40469 | VAChaRteMax |  | unimplemented | RW
40470 | VADisChaRteMax |  | unimplemented | RW
40471 | VNom |  | unimplemented | RW
40472 | VMax |  | unimplemented | RW
40473 | VMin |  | unimplemented | RW
40474 | AMax |  | unimplemented | RW
40475 | PFOvrExt |  | unimplemented | RW
40476 | PFUndExt |  | unimplemented | RW
40477 | IntIslandCat |  | unimplemented | RW
|  | UNCATEGORIZED | unimplemented
|  | INT_ISL_CAPABLE | unimplemented
|  | BLACK_START_CAPABLE | unimplemented
|  | ISOCH_CAPABLE | unimplemented
40478 | W_SF |  | 1 | R
40479 | PF_SF |  | unimplemented | R
40480 | VA_SF |  | 1 | R
40481 | Var_SF |  | unimplemented | R
40482 | V_SF |  | 0 | R
40483 | A_SF |  | -2 | R
40484 | S_SF |  | unimplemented | R

## 704
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40485 | ID |  | 704 | R | 704 | 704
40486 | L |  | 65 | R
40487 | PFWInjEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40488 | PFWInjEnaRvrt |  | supported | RW
|  | DISABLED | unimplemented
|  | ENABLED | supported
40489 | PFWInjRvrtTms |  | supported | RW | 0 | 60000
40491 | PFWInjRvrtRem |  | supported | R
40493 | PFWAbsEna |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40494 | PFWAbsEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40495 | PFWAbsRvrtTms |  | unimplemented | RW
40497 | PFWAbsRvrtRem |  | unimplemented | R
40499 | WMaxLimPctEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40500 | WMaxLimPct |  | supported | RW | 0 | 100
40501 | WMaxLimPctRvrt |  | supported | RW | 0 | 100
40502 | WMaxLimPctEnaRvrt |  | supported | RW
|  | DISABLED | unimplemented
|  | ENABLED | supported
40503 | WMaxLimPctRvrtTms |  | supported | RW | 0 | 60000
40505 | WMaxLimPctRvrtRem |  | supported | R
40507 | WSetEna |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40508 | WSetMod |  | unimplemented | RW
|  | W_MAX_PCT | unimplemented
|  | WATTS | unimplemented
40509 | WSet |  | unimplemented | RW
40511 | WSetRvrt |  | unimplemented | RW
40513 | WSetPct |  | unimplemented | RW
40514 | WSetPctRvrt |  | unimplemented | RW
40515 | WSetEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
40516 | WSetRvrtTms |  | unimplemented | RW
40518 | WSetRvrtRem |  | unimplemented | R
40520 | VarSetEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40521 | VarSetMod |  | supported | RW
|  | W_MAX_PCT | unimplemented
|  | VAR_MAX_PCT | unimplemented
|  | VAR_AVAIL_PCT | unimplemented
|  | VA_MAX_PCT | supported
|  | VARS | unimplemented
40522 | VarSetPri |  | supported | RW
|  | ACTIVE | unimplemented
|  | REACTIVE | supported
|  | VENDOR | unimplemented
40523 | VarSet |  | unimplemented | RW
40525 | VarSetRvrt |  | unimplemented | RW
40527 | VarSetPct |  | supported | RW | -60 | 60
40528 | VarSetPctRvrt |  | supported | RW | -60 | 60
40529 | VarSetEnaRvrt |  | supported | RW
|  | DISABLED | unimplemented
|  | ENABLED | supported
40530 | VarSetRvrtTms |  | supported | RW | 0 | 60000
40532 | VarSetRvrtRem |  | supported | R
40534 | WRmp |  | supported | RW | 1 | 1000
40535 | WRmpRef |  | supported | RW
|  | A_MAX | unimplemented
|  | W_MAX | supported
40536 | VarRmp |  | supported | RW | 1 | 1000
40537 | AntiIslEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
40538 | PF_SF |  | -4 | R
40539 | WMaxLimPct_SF |  | -2 | R
40540 | WSet_SF |  | unimplemented | R
40541 | WSetPct_SF |  | unimplemented | R
40542 | VarSet_SF |  | unimplemented | R
40543 | VarSetPct_SF |  | -2 | R
40544 | PFWInj.PF |  | supported | RW | 0.8 | 1
40545 | PFWInj.Ext |  | supported | RW
|  | OVER_EXCITED | supported
|  | UNDER_EXCITED | supported
40546 | PFWInjRvrt.PF |  | supported | RW | 0.8 | 1
40547 | PFWInjRvrt.Ext |  | supported | RW
|  | OVER_EXCITED | supported
|  | UNDER_EXCITED | supported
40548 | PFWAbs.PF |  | unimplemented | RW
40549 | PFWAbs.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented
40550 | PFWAbsRvrt.PF |  | unimplemented | RW
40551 | PFWAbsRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented

## 714
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40552 | ID |  | 714 | R | 714 | 714
40553 | L |  | 93 | R
40554 | PrtAlrms |  | unimplemented | R
40556 | NPrt |  | 3 | R
40557 | DCA |  | supported | R
40558 | DCW |  | supported | R
40559 | DCWhInj |  | unimplemented | R
40563 | DCWhAbs |  | unimplemented | R
40567 | DCA_SF |  | -2 | R
40568 | DCV_SF |  | -1 | R
40569 | DCW_SF |  | 1 | R
40570 | DCWH_SF |  | unimplemented | R
40571 | Tmp_SF |  | 0 | R
40572 | Prt.1.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
40573 | Prt.1.ID |  | supported | R
40574 | Prt.1.IDStr |  | unimplemented | R
40582 | Prt.1.DCA |  | supported | R
40583 | Prt.1.DCV |  | supported | R
40584 | Prt.1.DCW |  | supported | R
40585 | Prt.1.DCWhInj |  | unimplemented | R
40589 | Prt.1.DCWhAbs |  | unimplemented | R
40593 | Prt.1.Tmp |  | supported | R
40594 | Prt.1.DCSta |  | unimplemented | R
|  | OFF | unimplemented
|  | ON | unimplemented
|  | WARNING | unimplemented
|  | ERROR | unimplemented
40595 | Prt.1.DCAlrm |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | INPUT_OVER_VOLTAGE | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | BLOWN_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | ARC_DETECTION | unimplemented
|  | RESERVED | unimplemented
|  | TEST_FAILED | unimplemented
|  | INPUT_UNDER_VOLTAGE | unimplemented
|  | INPUT_OVER_CURRENT | unimplemented
40597 | Prt.2.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
40598 | Prt.2.ID |  | supported | R
40599 | Prt.2.IDStr |  | unimplemented | R
40607 | Prt.2.DCA |  | supported | R
40608 | Prt.2.DCV |  | supported | R
40609 | Prt.2.DCW |  | supported | R
40610 | Prt.2.DCWhInj |  | unimplemented | R
40614 | Prt.2.DCWhAbs |  | unimplemented | R
40618 | Prt.2.Tmp |  | supported | R
40619 | Prt.2.DCSta |  | unimplemented | R
|  | OFF | unimplemented
|  | ON | unimplemented
|  | WARNING | unimplemented
|  | ERROR | unimplemented
40620 | Prt.2.DCAlrm |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | INPUT_OVER_VOLTAGE | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | BLOWN_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | ARC_DETECTION | unimplemented
|  | RESERVED | unimplemented
|  | TEST_FAILED | unimplemented
|  | INPUT_UNDER_VOLTAGE | unimplemented
|  | INPUT_OVER_CURRENT | unimplemented
40622 | Prt.3.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
40623 | Prt.3.ID |  | supported | R
40624 | Prt.3.IDStr |  | unimplemented | R
40632 | Prt.3.DCA |  | supported | R
40633 | Prt.3.DCV |  | supported | R
40634 | Prt.3.DCW |  | supported | R
40635 | Prt.3.DCWhInj |  | unimplemented | R
40639 | Prt.3.DCWhAbs |  | unimplemented | R
40643 | Prt.3.Tmp |  | supported | R
40644 | Prt.3.DCSta |  | unimplemented | R
|  | OFF | unimplemented
|  | ON | unimplemented
|  | WARNING | unimplemented
|  | ERROR | unimplemented
40645 | Prt.3.DCAlrm |  | unimplemented | R
|  | GROUND_FAULT | unimplemented
|  | INPUT_OVER_VOLTAGE | unimplemented
|  | DC_DISCONNECT | unimplemented
|  | CABINET_OPEN | unimplemented
|  | MANUAL_SHUTDOWN | unimplemented
|  | OVER_TEMP | unimplemented
|  | BLOWN_FUSE | unimplemented
|  | UNDER_TEMP | unimplemented
|  | MEMORY_LOSS | unimplemented
|  | ARC_DETECTION | unimplemented
|  | RESERVED | unimplemented
|  | TEST_FAILED | unimplemented
|  | INPUT_UNDER_VOLTAGE | unimplemented
|  | INPUT_OVER_CURRENT | unimplemented

## 715
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
40647 | ID |  | 715 | R
40648 | L |  | 7 | R
40649 | LocRemCtl |  | unimplemented | R
|  | REMOTE | unimplemented
|  | LOCAL | unimplemented
40650 | DERHb |  | unimplemented | R
40652 | ControllerHb |  | unimplemented | RW
40654 | AlarmReset |  | unimplemented | RW
40655 | OpCtl |  | supported | RW
|  | STOP | supported
|  | START | supported
|  | ENTER_STANDBY | unimplemented
|  | EXIT_STANDBY | unimplemented