## Instructions
SunSpec PICS
This SunSpec PICS was generated by SunSpec Dashboard v3.7.5 based on the model contents of the connected device.
Most of the necessary information is populated but the PICS must be completed before submission by performing the following steps:
1. Examine the entry in the 'Value' column for each point to verify correctness:
- Common model (1) points that are implemented should contain the current value.
- All other model points that are implemented and have a variable value should contain the string 'supported'.
- All other model points that are implemented and have a constant value should contain the constant value.
It is assumed that scale factors are constants. If they are not, change the value to 'supported'.
- All unimplemented points should contain the string 'unimplemented'.
- For each enumeration or bit field entry that is not implemented, change the string to 'unimplemented'.
2. Examine the 'R/W' column to ensure the access is correct. It should be either 'R' or 'RW'.
3. Some points require a value range be specified. Points that have a grey background in the Min and Max column must
have a minimum and maximum value specified in the Min and Max columns. The value should be the value with the scale
factor applied. For example, a value specified in these fields would be 97.34 not 9734 if the scale factor is -2.
For models that have repeating elements, the value range is specified on the points in the first element and are
applicable for all of the repeating elements.
4. For any point that has an implementation deviation or special considerations indicate the issue in the 'Conformance Notes' column.
The certificate number will be filled in when certification is complete and this file will be archived with the Testing Info tab removed
along with a copy of the certificate on sunspec.org.

## Product and Testing Info
Product Information
Product Type | Inverter
Manufacturer Name | Guangdong Sofar Smart Solar Technology Co.,Ltd.
Product Name | Power Conversion System
Product Model Numbers | EBI44K-R-G2, EBI66K-R-G2, EBI87K-R-G2, EBI99K-R-G2, EBI124.9K-R-G2, EBI125K-R-G2, EBI150K-R-G2,EBI166K-R-G2, EBI250K-R-G2，EBI280K-R-G2, EBI300K-R-G2，EBI250K，EBI260K，EBI400K，EBI430K，EBI 99K-R, EBI 125K-R, EBI 215K-R, EBI 215K, EBI 1725K, ESS-215KLA-SA1, ESS-258KLA-SA1, ESS-261KLC-SA1, ESS-261KLC-SA2，ESS-261KLC-SA1-2H, ESS-261KLC-SA1-3H, ESS-261KLC-SA1-4H, ESS-261KLC-SA1-6H, ESS-1M04LC-SA1-2H, ESS-1M04LC-SA1-3H, ESS-1M04LC-SA1-4H, ESS-1M04LC-SA1-6H, ESS-1M04LC-SA1-8H, ESS-488KLH-SA1-2H, ESS-488KLH-SA1-3H, ESS-488KLH-SA1-4H, ESS-488KLH-SA1-6H, ESS-488KLH-SA1-8H, ESS-522KLI-SA1-2H, ESS-522KLI-SA1-3H, ESS-522KLI-SA1-4H, ESS-522KLI-SA1-6H, ESS-522KLI-SA1-8H, ESS-569KLJ-SA1-2H, ESS-569KLJ-SA1-3H, ESS-569KLJ-SA1-4H, ESS-569KLJ-SA1-6H, ESS-569KLJ-SA1-8H
Submitter Information
Full Name | Wang hui
Job Title | Certification Manager
Company Name | Guangdong Sofar Smart Solar Technology Co.,Ltd.
Relationship to Manufacturer | Employee
Email | wanghui@sofarsolar.com
Phone | +8615915311181
Device Under Test Information
Test Type | SunSpec Modbus Conformance Certification
Firmware Version Tested | V100015
Firmware Checksum (in hex) | 5848c2062968119914a1338347101806
Interface Type | RTU
If RTU
Interface Name | COM9
Unit ID | 1
Baud Rate | 9600
Parity | None
Timeout (secs) | 5
If Modbus TCP
IP Address | 58.251.3.210
IP Port | 30502
Unit ID | 1
If IEEE 2030.5
IP Address
IP Port
Poll Rate
Client PIN
Timeout (secs)
Reserved For SunSpec Alliance
SunSpec Certificate Number | SM-000054
Certificate Signer Name | Erin Mahan
Certificate Issued Date | 2026-05-29
Certificate Archive Location | https://sunspec.org/wp-content/uploads/2009/03/UPDATED_White-Label_SofarSolar_Modbus-2_Certificate_SM000054.pdf

## Manufacturer Attestation
Manufacturer Attestation
SofarSolar attests that subsequent software or firmware updates have not modified the tested SunSpec communication interface or affected its compliance with applicable SunSpec requirements.
Date: 2026/05/06
Name: Wang hui
E-mail: wanghui@sofarsolar.com

## Test Lab Settings
Target Definition | Target Definition Label | Param | Param Label | Param Value

## IEEE 1547 Electrical Test Setup
Test Category | Param Definition | Param Definition Label | Param | Param Label | Param Unit | Param Value

## 1
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50002 | ID |  | 1 | R | 1 | 1
50003 | L |  | 66 | R
50004 | Mn |  | Sofar | R
50020 | Md |  | ESI-12K-T1 | R
50036 | Opt |  | Sofar | R
50044 | Vr |  | V000304 | R
50052 | SN |  | ZD1057012KC23A010001 | R
50068 | DA |  | supported | RW | 1 | 247
50069 | Pad |  | 32768 | R

## 701
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50070 | ID |  | 701 | R | 701 | 701
50071 | L |  | 153 | R
50072 | ACType |  | supported | R
|  | SINGLE_PHASE | supported
|  | SPLIT_PHASE | supported
|  | THREE_PHASE | supported
50073 | St |  | supported | R
|  | OFF | supported
|  | ON | supported
50074 | InvSt |  | supported | R
|  | OFF | supported
|  | SLEEPING | supported
|  | STARTING | supported
|  | RUNNING | supported
|  | THROTTLED | supported
|  | SHUTTING_DOWN | supported
|  | FAULT | supported
|  | STANDBY | supported
50075 | ConnSt |  | supported | R
|  | DISCONNECTED | supported
|  | CONNECTED | supported
50076 | Alrm |  | supported | R
|  | GROUND_FAULT | supported
|  | DC_OVER_VOLT | supported
|  | AC_DISCONNECT | supported
|  | DC_DISCONNECT | supported
|  | GRID_DISCONNECT | supported
|  | CABINET_OPEN | supported
|  | MANUAL_SHUTDOWN | supported
|  | OVER_TEMP | supported
|  | OVER_FREQUENCY | supported
|  | UNDER_FREQUENCY | supported
|  | AC_OVER_VOLT | supported
|  | AC_UNDER_VOLT | supported
|  | BLOWN_STRING_FUSE | supported
|  | UNDER_TEMP | supported
|  | MEMORY_LOSS | supported
|  | HW_TEST_FAILURE | supported
|  | MANUFACTURER_ALRM | supported
50078 | DERMode |  | supported | R
|  | GRID_FOLLOWING | supported
|  | GRID_FORMING | supported
|  | PV_CLIPPED | supported
50080 | W |  | supported | R
50081 | VA |  | supported | R
50082 | Var |  | supported | R
50083 | PF |  | supported | R
50084 | A |  | supported | R
50085 | LLV |  | supported | R
50086 | LNV |  | supported | R
50087 | Hz |  | supported | R
50089 | TotWhInj |  | supported | R
50093 | TotWhAbs |  | supported | R
50097 | TotVarhInj |  | supported | R
50101 | TotVarhAbs |  | supported | R
50105 | TmpAmb |  | supported | R
50106 | TmpCab |  | supported | R
50107 | TmpSnk |  | supported | R
50108 | TmpTrns |  | supported | R
50109 | TmpSw |  | supported | R
50110 | TmpOt |  | supported | R
50111 | WL1 |  | supported | R
50112 | VAL1 |  | supported | R
50113 | VarL1 |  | supported | R
50114 | PFL1 |  | supported | R
50115 | AL1 |  | supported | R
50116 | VL1L2 |  | supported | R
50117 | VL1 |  | supported | R
50118 | TotWhInjL1 |  | supported | R
50122 | TotWhAbsL1 |  | supported | R
50126 | TotVarhInjL1 |  | supported | R
50130 | TotVarhAbsL1 |  | supported | R
50134 | WL2 |  | supported | R
50135 | VAL2 |  | supported | R
50136 | VarL2 |  | supported | R
50137 | PFL2 |  | supported | R
50138 | AL2 |  | supported | R
50139 | VL2L3 |  | supported | R
50140 | VL2 |  | supported | R
50141 | TotWhInjL2 |  | supported | R
50145 | TotWhAbsL2 |  | supported | R
50149 | TotVarhInjL2 |  | supported | R
50153 | TotVarhAbsL2 |  | supported | R
50157 | WL3 |  | supported | R
50158 | VAL3 |  | supported | R
50159 | VarL3 |  | supported | R
50160 | PFL3 |  | supported | R
50161 | AL3 |  | supported | R
50162 | VL3L1 |  | supported | R
50163 | VL3 |  | supported | R
50164 | TotWhInjL3 |  | supported | R
50168 | TotWhAbsL3 |  | supported | R
50172 | TotVarhInjL3 |  | supported | R
50176 | TotVarhAbsL3 |  | supported | R
50180 | ThrotPct |  | supported | R
50181 | ThrotSrc |  | supported | R
|  | MAX_W | supported
|  | FIXED_W | supported
|  | FIXED_VAR | supported
|  | FIXED_PF | supported
|  | VOLT_VAR | supported
|  | FREQ_WATT | supported
|  | DYN_REACT_CURR | supported
|  | LVRT | supported
|  | HVRT | supported
|  | WATT_VAR | supported
|  | VOLT_WATT | supported
|  | SCHEDULED | supported
|  | LFRT | supported
|  | HFRT | supported
|  | DERATED | supported
50183 | A_SF |  | -2 | R
50184 | V_SF |  | -1 | R
50185 | Hz_SF |  | -2 | R
50186 | W_SF |  | 1 | R
50187 | PF_SF |  | -2 | R
50188 | VA_SF |  | 1 | R
50189 | Var_SF |  | 1 | R
50190 | TotWh_SF |  | 2 | R
50191 | TotVarh_SF |  | 2 | R
50192 | Tmp_SF |  | 0 | R
50193 | MnAlrmInfo |  | supported | R

## 702
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50225 | ID |  | 702 | R | 702 | 702
50226 | L |  | 50 | R
50227 | WMaxRtg |  | 12000 | R
50228 | WOvrExtRtg |  | 9600 | R
50229 | WOvrExtRtgPF |  | 80 | R
50230 | WUndExtRtg |  | 9600 | R
50231 | WUndExtRtgPF |  | 80 | R
50232 | VAMaxRtg |  | 12000 | R
50233 | VarMaxInjRtg |  | 7200 | R
50234 | VarMaxAbsRtg |  | 7200 | R
50235 | WChaRteMaxRtg |  | 0 | R
50236 | WDisChaRteMaxRtg |  | 0 | R
50237 | VAChaRteMaxRtg |  | unimplemented | R
50238 | VADisChaRteMaxRtg |  | unimplemented | R
50239 | VNomRtg |  | 230 | R
50240 | VMaxRtg |  | 240 | R
50241 | VMinRtg |  | 220 | R
50242 | AMaxRtg |  | 20 | R
50243 | PFOvrExtRtg |  | 80 | R
50244 | PFUndExtRtg |  | 80 | R
50245 | ReactSusceptRtg |  | unimplemented | R
50246 | NorOpCatRtg |  | unimplemented | R
|  | CAT_A | unimplemented
|  | CAT_B | unimplemented
50247 | AbnOpCatRtg |  | unimplemented | R
|  | CAT_1 | unimplemented
|  | CAT_2 | unimplemented
|  | CAT_3 | unimplemented
50248 | CtrlModes |  | 1983 | R
|  | MAX_W | supported
|  | FIXED_W | supported
|  | FIXED_VAR | supported
|  | FIXED_PF | supported
|  | VOLT_VAR | supported
|  | FREQ_WATT | supported
|  | DYN_REACT_CURR | supported
|  | LV_TRIP | supported
|  | HV_TRIP | supported
|  | WATT_VAR | supported
|  | VOLT_WATT | supported
|  | SCHEDULED | supported
|  | LF_TRIP | supported
|  | HF_TRIP | supported
50250 | IntIslandCatRtg |  | unimplemented | R
|  | UNCATEGORIZED | unimplemented
|  | INT_ISL_CAPABLE | unimplemented
|  | BLACK_START_CAPABLE | unimplemented
|  | ISOCH_CAPABLE | unimplemented
50251 | WMax |  | supported | RW | 0 | 12000
50252 | WMaxOvrExt |  | unimplemented | RW
50253 | WOvrExtPF |  | unimplemented | RW
50254 | WMaxUndExt |  | unimplemented | RW
50255 | WUndExtPF |  | unimplemented | RW
50256 | VAMax |  | unimplemented | RW
50257 | VarMaxInj |  | unimplemented | RW
50258 | VarMaxAbs |  | unimplemented | RW
50259 | WChaRteMax |  | unimplemented | RW
50260 | WDisChaRteMax |  | unimplemented | RW
50261 | VAChaRteMax |  | unimplemented | RW
50262 | VADisChaRteMax |  | unimplemented | RW
50263 | VNom |  | unimplemented | RW
50264 | VMax |  | unimplemented | RW
50265 | VMin |  | unimplemented | RW
50266 | AMax |  | unimplemented | RW
50267 | PFOvrExt |  | unimplemented | RW
50268 | PFUndExt |  | unimplemented | RW
50269 | IntIslandCat |  | unimplemented | RW
|  | UNCATEGORIZED | unimplemented
|  | INT_ISL_CAPABLE | unimplemented
|  | BLACK_START_CAPABLE | unimplemented
|  | ISOCH_CAPABLE | unimplemented
50270 | W_SF |  | 0 | R
50271 | PF_SF |  | -2 | R
50272 | VA_SF |  | 0 | R
50273 | Var_SF |  | 0 | R
50274 | V_SF |  | 0 | R
50275 | A_SF |  | 0 | R
50276 | S_SF |  | 0 | R

## 704
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50277 | ID |  | 704 | R | 704 | 704
50278 | L |  | 65 | R
50279 | PFWInjEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50280 | PFWInjEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50281 | PFWInjRvrtTms |  | unimplemented | RW
50283 | PFWInjRvrtRem |  | unimplemented | R
50285 | PFWAbsEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50286 | PFWAbsEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50287 | PFWAbsRvrtTms |  | unimplemented | RW
50289 | PFWAbsRvrtRem |  | unimplemented | R
50291 | WMaxLimPctEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50292 | WMaxLimPct |  | supported | RW | 0 | 100
50293 | WMaxLimPctRvrt |  | unimplemented | RW
50294 | WMaxLimPctEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50295 | WMaxLimPctRvrtTms |  | unimplemented | RW
50297 | WMaxLimPctRvrtRem |  | unimplemented | R
50299 | WSetEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50300 | WSetMod |  | unimplemented | RW
|  | W_MAX_PCT | unimplemented
|  | WATTS | unimplemented
50301 | WSet |  | supported | RW | 0 | 12000
50303 | WSetRvrt |  | unimplemented | RW
50305 | WSetPct |  | supported | RW | 0 | 100
50306 | WSetPctRvrt |  | unimplemented | RW
50307 | WSetEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50308 | WSetRvrtTms |  | unimplemented | RW
50310 | WSetRvrtRem |  | unimplemented | R
50312 | VarSetEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50313 | VarSetMod |  | unimplemented | RW
|  | W_MAX_PCT | unimplemented
|  | VAR_MAX_PCT | unimplemented
|  | VAR_AVAIL_PCT | unimplemented
|  | VA_MAX_PCT | unimplemented
|  | VARS | unimplemented
50314 | VarSetPri |  | unimplemented | RW
|  | ACTIVE | unimplemented
|  | REACTIVE | unimplemented
|  | VENDOR | unimplemented
50315 | VarSet |  | supported | RW | -7200 | 7200
50317 | VarSetRvrt |  | unimplemented | RW
50319 | VarSetPct |  | supported | RW | -100 | 100
50320 | VarSetPctRvrt |  | unimplemented | RW
50321 | VarSetEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50322 | VarSetRvrtTms |  | unimplemented | RW
50324 | VarSetRvrtRem |  | unimplemented | R
50326 | WRmp |  | unimplemented | RW
50327 | WRmpRef |  | unimplemented | RW
|  | A_MAX | unimplemented
|  | W_MAX | unimplemented
50328 | VarRmp |  | unimplemented | RW
50329 | AntiIslEna |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50330 | PF_SF |  | -2 | R
50331 | WMaxLimPct_SF |  | -1 | R
50332 | WSet_SF |  | 2 | R
50333 | WSetPct_SF |  | -1 | R
50334 | VarSet_SF |  | 2 | R
50335 | VarSetPct_SF |  | -1 | R
50336 | PFWInj.PF |  | supported | RW | 0.8 | 1
50337 | PFWInj.Ext |  | supported | RW
|  | OVER_EXCITED | supported
|  | UNDER_EXCITED | supported
50338 | PFWInjRvrt.PF |  | unimplemented | RW
50339 | PFWInjRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented
50340 | PFWAbs.PF |  | unimplemented | RW
50341 | PFWAbs.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented
50342 | PFWAbsRvrt.PF |  | unimplemented | RW
50343 | PFWAbsRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented

## 713
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50344 | ID |  | 713 | R | 713 | 713
50345 | L |  | 7 | R
50346 | WHRtg |  | supported | R
50347 | WHAvail |  | supported | R
50348 | SoC |  | supported | R
50349 | SoH |  | supported | R
50350 | Sta |  | supported | R
|  | OK | supported
|  | WARNING | supported
|  | ERROR | supported
50351 | WH_SF |  | 0 | R
50352 | Pct_SF |  | 0 | R

## 714
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50353 | ID |  | 714 | R | 714 | 714
50354 | L |  | 118 | R
50355 | PrtAlrms |  | supported | R
50357 | NPrt |  | 4 | R
50358 | DCA |  | supported | R
50359 | DCW |  | supported | R
50360 | DCWhInj |  | supported | R
50364 | DCWhAbs |  | supported | R
50368 | DCA_SF |  | -2 | R
50369 | DCV_SF |  | -1 | R
50370 | DCW_SF |  | 1 | R
50371 | DCWH_SF |  | 2 | R
50372 | Tmp_SF |  | 0 | R
50373 | Prt.1.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
50374 | Prt.1.ID |  | supported | R
50375 | Prt.1.IDStr |  | supported | R
50383 | Prt.1.DCA |  | supported | R
50384 | Prt.1.DCV |  | supported | R
50385 | Prt.1.DCW |  | supported | R
50386 | Prt.1.DCWhInj |  | supported | R
50390 | Prt.1.DCWhAbs |  | supported | R
50394 | Prt.1.Tmp |  | supported | R
50395 | Prt.1.DCSta |  | supported | R
|  | OFF | supported
|  | ON | supported
|  | WARNING | supported
|  | ERROR | supported
50396 | Prt.1.DCAlrm |  | supported | R
|  | GROUND_FAULT | supported
|  | INPUT_OVER_VOLTAGE | supported
|  | DC_DISCONNECT | supported
|  | CABINET_OPEN | supported
|  | MANUAL_SHUTDOWN | supported
|  | OVER_TEMP | supported
|  | BLOWN_FUSE | supported
|  | UNDER_TEMP | supported
|  | MEMORY_LOSS | supported
|  | ARC_DETECTION | supported
|  | RESERVED | supported
|  | TEST_FAILED | supported
|  | INPUT_UNDER_VOLTAGE | supported
|  | INPUT_OVER_CURRENT | supported
50398 | Prt.2.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
50399 | Prt.2.ID |  | supported | R
50400 | Prt.2.IDStr |  | supported | R
50408 | Prt.2.DCA |  | supported | R
50409 | Prt.2.DCV |  | supported | R
50410 | Prt.2.DCW |  | supported | R
50411 | Prt.2.DCWhInj |  | supported | R
50415 | Prt.2.DCWhAbs |  | supported | R
50419 | Prt.2.Tmp |  | supported | R
50420 | Prt.2.DCSta |  | supported | R
|  | OFF | supported
|  | ON | supported
|  | WARNING | supported
|  | ERROR | supported
50421 | Prt.2.DCAlrm |  | supported | R
|  | GROUND_FAULT | supported
|  | INPUT_OVER_VOLTAGE | supported
|  | DC_DISCONNECT | supported
|  | CABINET_OPEN | supported
|  | MANUAL_SHUTDOWN | supported
|  | OVER_TEMP | supported
|  | BLOWN_FUSE | supported
|  | UNDER_TEMP | supported
|  | MEMORY_LOSS | supported
|  | ARC_DETECTION | supported
|  | RESERVED | supported
|  | TEST_FAILED | supported
|  | INPUT_UNDER_VOLTAGE | supported
|  | INPUT_OVER_CURRENT | supported
50423 | Prt.3.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
50424 | Prt.3.ID |  | supported | R
50425 | Prt.3.IDStr |  | supported | R
50433 | Prt.3.DCA |  | supported | R
50434 | Prt.3.DCV |  | supported | R
50435 | Prt.3.DCW |  | supported | R
50436 | Prt.3.DCWhInj |  | supported | R
50440 | Prt.3.DCWhAbs |  | supported | R
50444 | Prt.3.Tmp |  | supported | R
50445 | Prt.3.DCSta |  | supported | R
|  | OFF | supported
|  | ON | supported
|  | WARNING | supported
|  | ERROR | supported
50446 | Prt.3.DCAlrm |  | supported | R
|  | GROUND_FAULT | supported
|  | INPUT_OVER_VOLTAGE | supported
|  | DC_DISCONNECT | supported
|  | CABINET_OPEN | supported
|  | MANUAL_SHUTDOWN | supported
|  | OVER_TEMP | supported
|  | BLOWN_FUSE | supported
|  | UNDER_TEMP | supported
|  | MEMORY_LOSS | supported
|  | ARC_DETECTION | supported
|  | RESERVED | supported
|  | TEST_FAILED | supported
|  | INPUT_UNDER_VOLTAGE | supported
|  | INPUT_OVER_CURRENT | supported
50448 | Prt.4.PrtTyp |  | supported | R
|  | PV | supported
|  | ESS | supported
|  | EV | supported
|  | INJ | supported
|  | ABS | supported
|  | BIDIR | supported
|  | DC_DC | supported
50449 | Prt.4.ID |  | supported | R
50450 | Prt.4.IDStr |  | supported | R
50458 | Prt.4.DCA |  | supported | R
50459 | Prt.4.DCV |  | supported | R
50460 | Prt.4.DCW |  | supported | R
50461 | Prt.4.DCWhInj |  | supported | R
50465 | Prt.4.DCWhAbs |  | supported | R
50469 | Prt.4.Tmp |  | supported | R
50470 | Prt.4.DCSta |  | supported | R
|  | OFF | supported
|  | ON | supported
|  | WARNING | supported
|  | ERROR | supported
50471 | Prt.4.DCAlrm |  | supported | R
|  | GROUND_FAULT | supported
|  | INPUT_OVER_VOLTAGE | supported
|  | DC_DISCONNECT | supported
|  | CABINET_OPEN | supported
|  | MANUAL_SHUTDOWN | supported
|  | OVER_TEMP | supported
|  | BLOWN_FUSE | supported
|  | UNDER_TEMP | supported
|  | MEMORY_LOSS | supported
|  | ARC_DETECTION | supported
|  | RESERVED | supported
|  | TEST_FAILED | supported
|  | INPUT_UNDER_VOLTAGE | supported
|  | INPUT_OVER_CURRENT | supported

## 715
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50473 | ID |  | 715 | R
50474 | L |  | 7 | R
50475 | LocRemCtl |  | supported | R
|  | REMOTE | supported
|  | LOCAL | supported
50476 | DERHb |  | supported | R
50478 | ControllerHb |  | supported | RW
50480 | AlarmReset |  | supported | RW
50481 | OpCtl |  | supported | RW
|  | STOP | supported
|  | START | supported
|  | ENTER_STANDBY | supported
|  | EXIT_STANDBY | supported